## ToC 1
Volume II
Section 4: Tender Forms
Table of Contents
A | Price Schedule
B2 | Technical Data Schedule
Technical Data Schedule shall be submitted along with Technical Proposal

## ToC 2
Volume II
Section 4: Tender Forms
Table of Contents
A | Price Schedule
B2 | Technical Data Schedule
| 1 | A1. STP and Accessories
| 2 | A2. PSC and Accessories
| 3 | A3. MVCC and Hardware
| 4 | A4. Insulators
| 5 | A5. Stays
| 6 | B1. Distribution Transformer
| 7 | B2. 11 kV Switchgear
| 8 | B3. Cables
| 9 | B4. Lights
| 10 | C1. Aerial Bunched Cable

## A1. STP and Accessories
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A1 | Steel Tubular Pole and Accessories
1 | General
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable standard
Type
2 | Steel Lattice Tower |  | For use in Special Cases
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable Standard for Steel
| Are the poles fully Galvanized? | yes/no | Yes
| Applicable Standard for Galvanization |  | EN ISO 1461 or IS:4736 or an equivalent international standard
| Overall Length | m
| Design span or normal ruling span of Towers | m | 350
| Wind span and weight span of Conductor |  | 1.5 times of Span
| Design Working Load | kg
| Factor of Safety |  | 2
| Minimum Breaking Load | kg
| Overall Height | m
| Center to center between 2 tower legs | M
| Tower width at Ground Level | M
| Maximum width of tower(Foundation width per leg) | M
| Wind zone | 4 | 4, 5; As per IS 802
| Circuit on Towers |  | Single or double
| Angle of Deviation |  | As per site condition
| Phase to Phase Clearance - Horizontal | m | 2.75
| Phase to Phase Clearance - Vertical | m | 1.75
| Insulator Types |  | Disc
| Conductor |  | ACSR DOG/ ACSR WOLF
| Complete Earthing set as per specification provided | yes/no | yes
3 | Steel Tubular Pole
Manufacturer
Country of Origin
Years of Manufacturing Experience
| Reference Standard |  | IS 2713
| Pole Designation (as per IS 2713) |  | 410 SP-31, 410 SP-52, 410 SP-57, 410 SP-72, as required (available in IS 2713)
| Length of Poles | m | 9, 10, 11, 12, 13, 14.5
| Are the poles fully Galvanized? | yes/no | Yes
| Applicable Standard for Galvanization |  | ISO 1461 or IS:4736 or an equivalent international standard
| Approximate Weight (excluding the weight of galvanization, base plate and pole cap) | kg | As per IS 2713
| Planting Depth | m | As per Drawings
4 | Steel Cross Arm Channel and Angle Braces |  | To be completed for all types of components
Manufacturer
Country of Origin
| Reference Standard |  | IS: 2062-2011 and IS 808 -1989
| Dimensions |  | Adhering to Drawings and Detail Design by Contractor
| Is the cross arm and angles fabricated from hot-rolled steel sections? | yes/no | Yes
5 | Pole Clamps, Steel Bolts and Nuts
Manufacturer
Country of Origin
| Reference Standard |  | IS: 2062-2011 and IS 808 -1989
| Dimensions |  | Adhering to Drawings and Detail Design by Contractor and as required on the location of the Poles
| Is the cross arm and angles fabricated from hot-rolled steel sections? | yes/no | Yes
6 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
7 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## A2. PSC and Accessories
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A2 | PSC Pole and Accessories
1 | General
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable standard
Type
2 | PSC Poles
Manufacturer
Country of Origin
Years of Manufacturing Experience
| Governing Standard |  | IS 1678, ISO 6734, IS 1785
Length of PSC Pole
Approximate Weight of the Pole
Dimensions
Top Width
Bottom Width
Pole Thickness
Working Load
Ultimate Load
| Concrete Grade |  | M40
Pre-Stressing wire
| Governing Standard |  | IS 1785
| Diameter | mm | 7.9 mm (7/2.6mm)
No. of Tensioned Wire
| No. of Stirrups |  | 12
Cement specifications
Make
Grade
| Is Nepal Standard Certified? | yes/no | yes
Concrete quantity per pole
Steel quantity per pole
| Planting Depth |  | Adhering to Drawings and Detail Design by Contractor
3 | Steel Cross Arm Channel and Angle Braces |  | To be completed for all types of components
Manufacturer
Country of Origin
| Reference Standard |  | IS: 226-1975 and IS 808 -1964
| Dimensions |  | Adhering to Drawings and Detail Design by Contractor
| Is the cross arm and angles fabricated from hot-rolled steel sections? | yes/no | Yes
yes/no
4 | Pole Clamps, Steel Bolts and Nuts
Manufacturer
Country of Origin
| Reference Standard |  | IS: 2062-2011 and IS 808 -1989
| Dimensions |  | Adhering to Drawings and Detail Design by Contractor and as required on the location of the Poles
| Is the cross arm and angles fabricated from hot-rolled steel sections? | yes/no | Yes
5 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
6 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## A3. MVCC and Hardware
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A3 | MVCC and Hardware
1 | General
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable standard
Type
2 | Medium Voltage Covered Conductor
Manufacturer’s Name & Address
| List of Standard Applicable |  | En 50397-1: 2006
Rated Voltage, ≥ 11 kV
Conductors
| a. Material |  | All Almunium Alloy
| b. Actual Area (mm2) | sq. mm | 55/100/150
c. Stranding & wire diameter (Nos / mm)
d. Approximate overall diameter (mm)
e. Approximate weight (kg/km)
| f. Maximum Calculated D.C. resistance at 20°C (Ω/km) |  | As per Standard
g. Approximate calculated breaking load (kN)
h. Reactance per km (Ω/km)
i. Current Rating (Amps)
j. Lay ratio
k. Direction of lay
Wire (strand) used in the construction of conductors
a. Nominal Diameter (mm)
b. Maximum Diameter (mm)
c. Cross-section area of nominal diameter wire (mm2)
d. Weight (kg/km)
e. Maximum Calculated D.C. resistance at 20°C (Ω/km)
f. Minimum breaking load after stranding (kN)
Insulation (Semi-conduction screen)
a. Material
Insulation (Inner layer)
a. Material
b. Nominal thickness (mm)
c. Carbon Content (%)
Insulation (Outer layer)
a. Material
| b. Nominal thickness (mm) | mm
| c. Carbon Content (%) | %
| Combined insulation i.e. both layers | yes/no
a. Minimum thickness
b. Min. Tensile strength of insulation (N/mm2)
c. Elongation (min)
d. Volume resistivity
i. At room temperature of 27 °C (Ω-cm)
ii. At 70°C (Ω-cm)
e. Hot set
i. Max. Elongation under load (%)
ii. Max. Permanent elongation (%)
f. High Voltage water immersion Test (4 kV AC for 5 minutes)
Covered Conductor
a. Minimum Breaking Strength (kN)
b. Short time current rating: 1 sec (kA)
c. Maximum conductor operating temperature
i. Continuous operation (°C)
ii. Emergency operation (°C)
iii. Short circuit operation; 5 sec (°C)
d. Overall diameter (mm)
e. Approximate weight of complete cable (kg/km)
f. Maximum DC resistance of conductor at 20 °C (Ω/km)
h. Reactance per km (Ω/km)
Size of cable drum
Approximate Length of conductor per drum (km ± %)
3 | Tension/Anchoring Assembly
Name of Supplier
Standards
Type of Design
Weight
Cable Range
| 50 sq mm cable | mm | Φ13-16 mm
| 100 sq mm cable | mm | Φ17-19 mm
| 150 sq mm cable | mm
Material
Ultimate Tensile Strength
| 50 sq mm cable | kN | 20
| 100 sq mm cable | kN | 30
| 150 sq mm cable | kN
| Installation (with/without disassembly) |  | Ready to use (without disassembling)
Marking
Dimensions
4 | Polymeric Cable Ties
Name of Supplier
Standards
Length
Weight
| Cable Range |  | 50 mm2 cable (Φ13-16 mm); 100 mm2 cable (Φ17-19 mm)
Material
| Installation (with/without disassembly) |  | Ready to use (without disassembling)
Marking
5 | IPC
Name of Supplier
Standards
| Type of IPC |  | Type – 1: Bare to Covered Conductor
Type – 2: Covered to Covered Conductor
Type – 3: Tapping Connector
| Are torque limiting shear heads provided to tightening bolts? |  | Yes
Tightening Torque
| Torque for establishing connection between main and Tap (Nm) |  | 70% of minimum torque specified
| Cable Range |  | 50 mm2 cable (Φ13-16 mm)
100 mm2 cable (Φ17-19 mm)
Marking
6 | Straight-through Jointing
Name of Supplier
Type No
| Size Range |  | 50 mm2 cable (Φ13-16 mm)
100 mm2 cable (Φ17-19 mm)
| Is any metallic part carrying potential in operation exposed during installation? |  | No
| Installation |  | Crimping by Hexagonal Compression
7 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
8 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## A4. Insulators
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A4 | Insulators
1 | Pin Insulator
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standards |  | IS 731-1971, IS 2486, IEC 60815
| Marking as per specifications | yes/no | Yes
| Highest system voltage | kV | 12
| Rated voltage | kV | 11
| Creepage distance (minimum) | mm
| Wet power frequency withstand voltage | kV
| Impulse withstand voltage | kV
| Puncture power frequency voltage (minimum) | kV
| Visible discharge voltage (Effective) | kV
| Cantilever strength | kN
| GI pin head |  | Small S165P or Large
2 | Disc Insulator
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standards |  | IS 731-1971, IS 2486, IEC 60815
| Marking as per specifications | yes/no | Yes
| Highest system Voltage | kV | 12
| Rated Voltage | kV | 11
| Porcelain Diameter (minimum) | mm
| Spacing | mm
| Creepage Distance (minimum) | mm
Power Frequency Puncture withstand Voltage
| Wet Power Frequency Withstand Voltage | kV
| Impulse Withstand Voltage | kV
| Puncture Power Frequency Voltage (minimum) | kV
| Visible Discharge Voltage | kV
| Mechanical Strength | kN
Ball and Socket Size
| Applicable Standard for Special Characteristics |  | IS: 3188-1980
3 | Disc Insulator Fittings
Manufacturer
| Country of Origin | yes/no
Years of Manufacturing Experience
Model No.
| Applicable Standard |  | IS: 2486
| Steel Classification |  | As per specification
| Ferrous parts are galvanized As per IS 2629 – 1985? | yes/no | Yes
| Thickness of Galvanizatiioin | micron
| Cotter Pins are Stainless Steel? | yes/no | Yes
| Ultimate Strength of Fittings | kN
4 | Insulator Pins
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standard |  | IS: 2486
| Type of steel used |  | Hot rolled steel
| Head type |  | Small S165P
| Total length | mm | 315
| Stalk length | mm | 165
| Shank length | mm | 150
| Minimum failing load | kN | 5
5 | Pin Insulator Tie
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Material Description furnished? | yes/no | yes
Aluminum clad steel wire
| Bidder Certitifies that all items offered are suitable for use with ACSR "DOG" and "WOLF" conductors? | yes/no | yes
| Bidder Certitifies that all items offered are suitable for use with insulators specified in specifications? | yes/no | yes
| Holding Rating of Top tie for "DOG" | kg
| Holding Rating of Double support Top tie for "DOG" | kg
| Holding Rating of Side tie for "DOG" | kg
| Holding Rating of Double support Side tie for "DOG" | kg
| Holding Rating of Top tie for "WOLF" | kg
| Holding Rating of Double support Top tie for "WOLF" | kg
| Holding Rating of Side tie for "WOLF" | kg
| Holding Rating of Double support Side tie for "WOLF"" | kg
6 | Steel Wire Strand Grip
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Material Description furnished? | yes/no | yes
| Bidder Certitifies that steel strand grip offered is suitable for use with insulator; stay set and stay wire specified in specifications? | yes/no | yes
| Holding Rating of Grip for 7/8 SWG | kg
| Holding Rating of Grip for 7/8 SWG | kg
7 | Shackle Insulators
Manufacturer
| Catalog/Dimensional drawings |  | Yes
| Governing Standards |  | Yes
| Copies of Standards Attached: |  | Yes
| If not IS Standards, are standards used equivalent? |  | Yes
| Copies of alternate standards attached? |  | Yes
Ratings:
| Highest system Voltage | kV | 1
| Rated Voltage | kV | 0.5
Power frequency withstand voltage, 1 min
| Dry | kV | 23
| Wet | kV | 10
| Power Frequency Puncture withstand Voltage, 1 min | kV | 1.3xActual dry
flashover voltage
| Leakage distance | mm | 65 min.
| Mechanical Strength | kN | 11.5
| IS Type |  | 1
| Approximate Weight | kg
mandatorily
8 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
9 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## A5. Stays
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A5 | Stays
1 | Stay
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
Applicable Standards
| Marking as per specifications | yes/no | Yes
| Length of stay rod | m | 2.44
| Diameter of stay rod | mm | 19
| Ultimate tensile strength of stay rod and turn-buckle | kg/sq cm | 4200
| Minimum breaking load | kg | 6433
| Length of threaded portion | mm | 300
| Thimble shape |  | Suitable for Stay wire of 7/10, 7/8, 19/8 and as per approved design
| Thimble section |  | 18 SWG min.
| Stay plate section | mm | 300 x 300 x 6
| Eyebolt length | mm | 300
| Eyebolt diameter | mm | 16
2 | Stay Wire
Manufacturer
Country of Origin
Years of Manufacturing Experience
| Applicable Standard |  | IS 2141-2000
| Applicable Standard for galvanization |  | IS 4826-1979, BS 183-1972
| Steel Wire Size | (Nos of wire/ SWG) | 7/10, 7/8, 19/8 or as per approved design
| No. of Wire | Nos | 7, 19 or as per approved design
| Diameter of Each wire | mm | As per SWG
| Strand Diameter (Overall) | mm
| Overall Cross Sectional Area | sq mm
| Steel Quality |  | Gr. 700
| Minimum Tensile Strength of Steel | N/sq mm | 700
| Ultimate Tensile Strength | N/sq mm
| Min. Breaking load of single wire | kN | 3.71
| Min. Breaking load of strand | kN | 26
| Approximate Weight | kg/km
| Minimum weight of Wire in each reel | kg | 100
| Left hand Lay | yes/no | Yes
| Minimum Weight of Zinc Coating | g/sq mm | As per IS 4826-1979, BS 183-1972
3 | Stay Insulator
| Manufacturer | yes/no
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standard |  | IS: 5300-1969
| Marking as per specification? | yes/no | Yes
| IS Designation |  | C
| Length | mm | 140
| Diameter | Mm | 85
| Cable Hole Diameter | mm | 25
| Creepage Distance (minimum) | mm | 57
| Minimum failing load | kN | 88
Power Frequency Withstand Voltage
| Dry | kV | 27
| Wet | kV | 13
4 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
5 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## B1. Distribution Transformer
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A | Distribution Transformer
1 | General
Manufacturer
Place of manufacture/ testing
| Applicable Standards |  | IEC 60076
| Type |  | Three Phase
| Winding material |  | Copper
| Primary Winding BIL | kV | 75
| Primary Bushing BIL | kV | 75
Accessories listed below furnished?
| a) Lower oil filter valve |  | Yes
| b) Liquid level gauge |  | Magnetic-type, readable from the ground level
| c) Lifting lugs |  | Yes/No
| d) Name Plate |  | Yes/No
| e) Tank earthing terminal |  | Suitable for grounding cable with # 6 SWG solid/stranded copper
| f) Lightning Arrester | yes/no | Yes
| g) HV Fuses | yes/no | Yes
MCCB
| (i) Overload Protection | yes/no | Yes
| (ii) Short-circuit Protection | yes/no | Yes
| (iii) Provision for auxiliary contacts | yes/no | Yes
2 | Design Information
| a) Rated kVA | kVA | 25, 50, 100, 200, 300
| b) Number of phases |  | Three for 3- ø
| c) Frequency (Hz) |  | 50
| d) Voltage ratio at no load (kV) | kV | 11/0.4 for 3-ø
| e) Winding connections |  | Dyn11 (for 3-ø)
| f) Core Material used and Grade |  | CRGO
g) Magnetising current at normal ratio:
(i) HV (A)
(ii) LV (A)
h) Maximum flux density in core iron at normal voltage and frequency based on the net section of iron:
| (i) Cores (T) | T | 1.6
| (ii) Yokes (T) | T | 1.6
i) Type of winding:
| (i) HV (A) | A
| (ii) LV (A) | A
j) Maximum current density in winding at rated power:
| (i) HV (A/mm2) | A/sq mm | 2.5
| (ii) LV (A/mm2) | A/sq mm | 2.5
| k) Type of insulation used for: | yes/no
(i) HV winding
(ii) LV winding
l) No load loss at normal voltage ratio and 75oC (Watt)
m) Load loss at rated current and at 75oC (Watt)
n) Regulation at 75oC and rated power as a percentage of normal voltage:
(i) at 1 p.f. (%)
(ii) at 0.8 p.f. (%)
o) Impedance voltage at 75oC and rated power:
(i) at normal tapping (%)
(ii) at -5% tapping (%)
(iii) at +5% tapping (%)
p) Efficiency at:
(i) 1 p.f. 125% load and rated current (%)
(ii) 1 p.f. 100% load and rated current (%)
(iii) 1 p.f. 75% load and rated current (%)
(iv) 1 p.f. 50% load and rated current (%)
(v) 1 p.f. 25% load and rated current (%)
q) Load at which maximum efficiency will occur (kVA)
r) Maximum Efficiency (%)
s) Temperature rise at rated kVA by thermometer in oil (oC)
t) Temperature rise at rated kVA by resistance of windings (oC)
u) Permissible overload (%)
v) Transformer insulating oil specification:
(i) Total volume of insulating oil at 20oC (litre)
(ii) Effective expansion capacity of conservator in litre as well as percentage
w) Approximate weight and dimensions:
(i) Weight of core (kg)
(ii) Weight of winding (kg)
(iii) Weight of tank and fittings (kg)
(iv) Weight of oil (kg)
(v) Total weight (kg)
x) Radiator details:
(i) No of radiators per transformer (No.)
(ii) No of fins per radiator (No.)
(iii) Width of each fin (mm)
(iv) Thickness of radiator (mm)
y) Tank Dimensions:
(i) Length (mm)
(ii) Breadth (mm)
(iii) Height (mm)
(iv) Tank Sheet Thickness (sides x bottom x top) (mm)
z) Approximate dimensions including fittings:
(i) Overall length (mm)
(ii) Overall width (mm)
(iii) Overall height (mm)
aa) Winding resistance value at 75oC
(i) Per phase resistance of HV winding
(ii) Per phase resistance of HV winding
3 | Testing Facilities available in the Lab of the Manufacturer |  | Include Name of Test Equipment/Facility, Date of Calibration and Calibrated by
Applied voltage test
Induced voltage test
No load loss and excitation current test
Impedance voltage and load loss tests
Resistance measurement
Ratio tests
Polarity and phase relation tests
Leakage tests
Insulation resistance tests
(i) Temperature rise test
(ii) Dielectric Type test
(iii) Tank pressure test
4 | MCCB and LVCT Information
| IP class of Distribution Box |  | IP 54
Name of Manufacturer
| MCCB: |  | ABB/Siemens/Schneider/GE/L&T/Hyundai/Mitsubishi/Legrand or equiv.
| LVCT: |  | ABB/Siemens/Schneider/GE/L&T/Hyundai/Mitsubishi/Legrand or equiv.
| If MCCB and LVCT are of other company, then will a type test shall be carried out free of cost in a third party lab accredited by ILAC/IAF? |  | Yes
5 | Remote Data Logging System
| IP class of Enclosure Box |  | IP 67
| Over Current Protection |  | Available
| Surge Current Protection |  | Available
| Positioning System |  | GPS
| Data Connection System |  | GPRS/3G
| Temperature Sensor |  | Available
| Oil level Sensor |  | Available
| Current Transformer |  | Available with 0.2 Class for Metering
| Potential Transformer |  | Available with 0.2 Class for Metering
| Voltage Measurement |  | Xformer Secondary and MCCB Outputs
| Current Measurement |  | Xfomer Secondary
6 | Information to be Submitted with the Tender
Dimension drawing showing the main dimensions nd physical arrangements of major components
Detailed descriptions or leaflets of:
- Arrangement and insulation of windings
- Core and tank
- Measuring/ monitoring instruments
- Transformer auxiliaries
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required rating | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
7 | Informative Data
Manufacturer
Place of Manufacturing
| Main Dimensions (W x D x H) | m
| Main Dimensions for transportation (W x D x H) | m
| Weight of the transformer inclusive of oil and accessories | t
| Oil weight | t
| Weight for transportation | t
Maximum permitted acceleration during transport
| Lengthwise (x) | m/s2
| Crosswise (y) | m/s2
| Vertical (z) | m/s2

## B2. 11 kV Switchgear
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
B2 | 11 kV Switchgear
1 | Drop Out Fuse
Name and Address of Manufacturer
| Applicable Standard |  | IEC 60282
| Type of DO Fuse |  | Expulsion, Class A
| Rated Voltage | kV | 12
| Service Voltage | kV | 11
| Rated Frequency | Hz | 50
| No. of D.O. Fuse unit per set | Nos | 3
| Rated Continuous Current | A | 100
| Switching Voltage (max) | kV
Dry Impulse withstand (1.2 kV/50μs) voltage (positive & negative polarity) (Peak)
| i. Across the isolating distance of the fuse base | kV | 85
| ii. To Earth and between poles | kV | 75
Wet 1 min. power frequency withstand voltage (rms)
| i. Across the isolating distance of the fuse base | kV | 32
| ii. To Earth and between poles | kV | 28
| Total Creepage distance (min) | mm | 320
Interrupting rating
| i. Symmetrical interrupting rating (min) rms | kA | 8
| ii. Asymmetrical interrupting rating (min) rms | kA | 9.6
iii. X/R Ratio
Temperature Rise Limit (in Air)
| i. Copper contacts silver faced | ° C | 65
| ii. Terminals | ° C | 50
iii. Spring: The temperature shall not such a value that elasticity of the Metal is changed.
| Mounting angle (to vertical plane) | ° (deg)
| Length of the Fuse barrel | mm | 285 ± 2
| Diameter of the Fuse barrel | mm
| Tensile Strength | kN | 10
| Thickness of Galvanization |  | As per IEC
| Mounting Bracket GI ‘L’ shape with two bolts | mm | 200 x 200
Approximate weight
| i. Porcelain Fuse Base (with embedded parts) | Kg
| ii. Lower and Upper metal portion of Fuse Base | Kg
| iii. Fuse Carrier | Kg
| iv. Upper and Lower metal portion of fuse carrier | kg
| Declaration to carry out Type Test after mass production in the third-party lab as per Clause 9. | Y/N | Yes
2 | Lightning Arrester
Name and Address of Manufacturer
Applicable Standard
| Type of Lightning Arrester | yes/no | Gapless Metal-Oxide Polymeric
| Rated Voltage | kV (rms) | 12
| Continuous Operating Voltage | kV (rms) | 9
| Rated Frequency | Hz | 50
| No. of L. A. unit per set | Nos | 3
| Nominal discharge current, 8/20 μs | kA (rms) | 10
| Energy Absorption Capacity | kJ/kV | >6
| Long duration discharge class | Class
| High Current Impulse (4/10μs) – Peak | kA | 100
| Steep Current maximum impulse residual voltage (1/20μs) | kV | 40
Impulse Residual Voltage - Peak
| i. Maximum Residual Voltage at 10 kA for 8/20μs | kV | 35
| ii. Switching impulse (30-100/60-200μs) maximum residual voltage | kV | 30
| One second TOV withstand capability | kV | > 1.15 x 12
| Type of Housing Insulator |  | Polymeric
Insulation withstand level
| i. Lighting Impulse (1.2/50 μs) voltage – peak | kV | 75
| ii. Power Frequency withstand voltage (wet) | kV | 28
| Total Creepage distance (min) | mm | 320
| Energy Absorption Capability (with 4/10 wave) | kJ/kV | > 3.2
Insulating Bracket
| i. Power Frequency withstand voltage | kV | 20
| ii. Cantilever strength | Nm
| Approximate Weight of a Unit | kg
| Declaration to carry out Type Test after mass production in the third-party lab as per Clause 9. | Y/N | Yes
3 | Load Break Switch
Name and address of Manufacturer
Country of Origin
Applicable Standards
Type of Design
Basic Ratings
| a. Maximum system voltage |  | 12
| b. Rated continuous current |  | 200/400/530/630/800/1250
| c. Rated frequency |  | 50 Hz
| d. Rated short time withstand current |  | 20 kA
| e. Rated peak withstand current |  | 25 kA
| Breaking Medium |  | Air
Making and Breaking Capacity
a. Mainly active load current
b. Number of load-break operations
c. Short circuit making current (peak)
d. Number of making operations
e. Cable charging current
f. Line charging current
| Rated Power frequency withstand voltage | kV | 28
| Impulse withstand voltage, kV | kV | 50
Other ratings and Specifications
a. Internal arc test
| b. Arc Extinction medium |  | As per IEC
c. Insulation medium
| d. Creepage distance | mm | As per IEC
Protection level (IP)
| a. Leak proof tank |  | IP 67
| b. Mechanism |  | IP 45
| c. Control box |  | IP 55
Operation Performance
a. Closing/Opening Time
| b. Mechanical Operations |  | 10000
| c. Operating temperature | deg C | -5 to +40
Gas Pressure
a. Nominal Pressure (atm at 20°C)
b. Bursting Pressure (atm)
c. Minimum Gas Pressure (atm)
d. Leakage rate (cc/sec)
Weight (approx.)
| Cable/Conductor Range | sq mm | 25 - 150
| Enclosure Material |  | Stainless steel
| Installation (with/without disassembly) |  | Ready to use (without disassembling)
Marking
Dimensions
4 | Information to be Submitted with the Tender
Dimension drawing showing the main dimensions nd physical arrangements of major components
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required rating | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
5 | Informative Data
Manufacturer
Place of Manufacturing
| Main Dimensions (W x D x H) | m
| Main Dimensions for transportation (W x D x H) | m
| Weight of the transformer inclusive of oil and accessories | t
| Oil weight | t
| Weight for transportation | t
Maximum permitted acceleration during transport
| Lengthwise (x) | m/s2
| Crosswise (y) | m/s2
| Vertical (z) | m/s2

## B3. Cables
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
B3 | CABLES
1 | 11 kV XLPE Cables
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable standard |  | IEC 60502, IEC 60228
Cable Type Designation
| Rated Voltage | kV | 11
| Maximum System Voltage | kV | 12
| Rated Voltage between conductor and screen | kV | 6
| Rated Voltage between two conductors | kV | 10
| Power Frequency Withstand Voltage | kV | 28
| Impulse Withstand Voltage (BIL) | kV | 75
Conductor
| Conductor Material |  | EC Grade Aluminum or EC Grade Annealed Copper
| Cross section of the Conductor | sq. mm.
| Is Conductor Stranded? | (yes/no) | yes
Stranded Conductor
i) Number of strands in each core
| ii) Size of strand | Sq. mm.
| iii) Maximum DC Resistance at 20 deg. C | Ohm/km
iv) Class of Stranding
| Number of Cores |  | One/Three/As per SLD
Insulation
| Insulation material and Type Designation |  | XLPE
XLPE Compound manufacturer
| Minimum thickness of insulation | mm | 3.4
| Minimum volume resistivity at 27 deg. C, 70 deg. C and 90 deg. C | Ohm-cm
Sheath
Material for inner sheath, type of sheathing and Type Designation
| Minimum thickness of inner sheath | mm
Material for outer sheath, type of sheathing and Type Designation
| Minimum thickness of outer sheath | mm
Armor
Material
Shape
| Dimension | mm
Conductor Screen
Material
| Thickness | mm
| Insulation Screen | yes/no
Material
| Thickness | mm
Metallic Layer/Screen
Type
Material
| Thickness | mm
| Overall Diameter of the Cable | mm
| Geometric Mean Radius (GMR) of the Cable/Conductor | mm
| Minimum Bending Radius | mm
| Insulation Resistance at 27 deg. C | Ohm/km
| Capacitive Reactance | Ohm/km
| Inductive Reactance | Ohm/km
Conductor Temperature rise during
| Normal Operation | deg. C | 90
| Short Circuit | deg. C | 250
Continuous Current Carrying Capacity
| Continuous Current Carrying Capacity in air and Corresponding assumptions/Conditions of installation | A
| Continuous Current Carrying Capacity under ambient temperature | A
| Continuous Current Carrying Capacity under Cable laid in Covered cable trenches | A
| Continuous Current Carrying Capacity under 3-6 Cables per tray touching each other in Covered cable trenches | A
| Continuous Current Carrying Capacity under ambient temperature for Cable laid in ground | A
Short circuit current
| Short circuit current for 0.1 sec | kA
| Short circuit current for 1.0 sec (minimum kA) | kA | 25
| Short circuit current for armor 1.0 sec (minimum kA) | kA
| Minimum tensile strength of insulation | kg/sq. cm
| Minimum elongation at break | %
| Minimum tensile strength of sheath | kg/sq. cm
| Minimum elongation at break | %
| Minimum tensile strength of armor | kg/sq. cm
| Minimum elongation at break | %
| Weight of Cable per km | kg/km
| Standard length of Cable per drum | m | min. 500m
| Net weight of cable in drum | kg
Method of Core identification
For Cables up to Five Cores
For Cable with more than Five Cores
Details of Anti Termite Covering
| Longitudinal water tight | yes/no | yes
| Fire Retardant | yes/no | yes
| Moisture Resistant | yes/no | yes
Please indicate in YES or NO whether the following tests have been carried out
| Ageing Test | yes/no | yes
| Loss of Mass Test | yes/no | yes
| Cold Impact Test | yes/no | yes
| Heat Shock Test | yes/no | yes
| Fire Retardant Test | yes/no | yes
Delivery of equipment following award of contract and approval of drawing
| ISO 9001 holder (including design) | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
Details of Marking on Outer Sheath
2 | 1100 V LV Power Cables
Manufacturer
Type of designation
| Standards |  | IEC
| Rated voltage | V | 1100
| Continuous permissible current (in air) | A
Maximum temperature of conductor during
| - continuous operation | °C | 90
| - short circuit duty for 1 s | °C | 250
| Conductor material |  | EC Grade Annealed Copper
| Insulation material |  | Polyethylene
Sheath material
Shield material
Armour material
| Number of cores | pcs
| Conductor cross section | mm2
Test voltages
| - power frequency withstand | kV
| - direct current | kV
| Nominal bending radius | mm
| Outer cable diameter | mm
| Standard Length of Cable Drum | m | min. 500
| Resistance of 1 m | ohm/m
| Reactance of 1 m | ohm/m
| Insulation Resistance at 27 deg. C | ohm
3 | Control Cables
Manufacturer
Type of designation
| Standards |  | IEC
| Rated voltage | V | 1100
| Test voltage | kV
| Conductor material |  | EC grade annealed Copper
Conductor insulation material
Shield material
Shield Insulation material
Cable sheath material
| Number of cores | pcs
| Conductor cross section | sq. mm
| Minimum bending radius | mm
| Outer cable diameter | mm
| Resistance of 1 m | ohm/m
| Reactance of 1 m | ohm/m
4 | Communication Cables
Manufacturer
Type of designation
| Standard |  | IEC
| Conductor material |  | EC grade annealed Copper
| Conductor diameter | mm
5 | Cable Trays an Accessories
Manufacturer
Type of designation
Material
Type of corrosion protection
6 | Cable Termination Kit |  | To be submitted separately for all kits
Manufacturer
Applicable standard
Type
Insulation level
Maximum design voltage
Impulse withstand voltage(BIL)
| Fire resistance treated | yes/no | yes
| Smoke resistance treated | yes/no | yes
| Stress relief performed | yes/no | yes
| Installation Instruction attached | yes/no | yes
List of Installation Accessories Supplied
7 | Information to be submitted along with bid
| ISO 9001 holder (including design) | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
8 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## B4. Lights
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
B4 | Lighting System
1 | Street Lighting Fixture Type 6
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
2 | Switches
Manufacturer
Type
| Protection Class | IP
3 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## C1. Aerial Bunched Cable
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
C | LT System
1 | Aerial Bunched Cables
Manufacturer’s Name & Address
List of Standard Applicable
Number of Cores
| a. Power Core (kg/km) | kg/km
| b. Neutral-cum-messenger core (kg/km) | kg/km
Power Core Conductors
| a. Nominal cross-sectional area (mm) | mm
| b. No. of strands (Nos) | nos.
| c. Diameter of strands (mm) | mm
Neutral-cum-messenger core
a. Nominal cross-sectional area
b. No. of strands
c. Diameter of strands
Max. DC resistance of conductor at 20°C
| a. Power Core (Ω/km) | Ω/km
| b. Neutral-cum-messenger core (Ω/km) | Ω/km
Approximate diameter of conductor
| a. Power Core (mm) | mm
| b. Neutral-cum-messenger core (mm) | mm
Approximate diameter with insulation
| a. Power Core (mm) | mm
| b. Neutral-cum-messenger core (mm) | mm
| Tensile strength of Power Core (N/mm2) | N/sq mm
| Minimum Breaking Load of Neutral-cum-messenger core (kN) | kN
Insulation minimum thickness
| a. Power Core (mm) | mm
| b. Neutral-cum-messenger core (mm) | mm
Approximate weight
| a. Power Core (kg/km) | kg/km
| b. Neutral-cum-messenger core (kg/km) | kg/km
| c. Overall AB Conductor (kg/km) | kg/km
Continuous current carrying capacity of cable in air at ambient temperature of 40°C
a. Power Core
b. Neutral-cum-messenger core
Derating Factor: Derating factors for variation in air temperature
Air Temperature °C
Laying
Conductor Materials
a. Power Core
| b. Neutral-cum-messenger core | yes/no
Raw Material sources
a. Aluminium
b. Alloy Aluminium
c. XLPE
Insulation
a. Core identification
b. Min. Tensile strength of insulation (N/mm2)
c. Elongation (min)
d. Volume resistivity
| i. At room temperature of 27 °C (Ω-cm) | Ω-cm
| ii. At 70°C (Ω-cm) | Ω-cm
e. Hot set
| i. Max. Elongation under load (%) | %
| ii. Max. Permanent elongation (%) | %
f. High Voltage Test (3 kV AC for 5 minutes)
g. Bending Test (No cracks visible to the naked eye)
| Approximate Length of bundled Cable per drum (km ± %) | km
2 | Information to be Submitted with the Tender
Dimension drawing showing the main dimensions nd physical arrangements of major components
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
3 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm