## ToC 1
Volume II
Section 4: Tender Forms
Table of Contents
A | Price Schedule
B2 | Technical Data Schedule
Technical Data Schedule shall be submitted along with Technical Proposal

## ToC 2
Volume II
Section 4: Tender Forms
Table of Contents
A | Price Schedule
B2 | Technical Data Schedule
| 1 | A1. 33 kV Poles and Accessories
| 2 | A2. ACSR Conductor and Hardware
| 3 | A3. Insulators
| 4 | A4. Stays
| 5 | A5. ADSS
| 6 | B1. Power Transformer
| 7 | C1. 33 kV System
| 8 | C2. 33 kV Indicating Instrument
| 9 | C3. 33 kV Protection Relay
| 10 | D1. 12 kV System
| 11 | D2. 12 kV Indicating Instrument
| 12 | D3. 12 kV - Protective Relay
| 13 | E1. Station Transformer
| 14 | E2. ACDB
| 15 | F1. Battery System
| 16 | F2. DCDB
| 17 | G1. Cables
| 18 | G2. Under Ground Cable
| 19 | H1. Substation Auxiliaries
| 20 | H2. SAS System
| 21 | H3. Protection System
| 22 | H4. Communication System
| 23 | I1. Earthing System
| 24 | J1. Illumination System
| 25 | K1. Miscellaneous

## A1. 33 kV Poles and Accessories
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A1 | 33 kV Poles and Accessories
1 | General
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable standard
Type
2 | Steel Lattice Tower
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable Standard for Steel
| Are the poles fully Galvanized? | yes/no | Yes
| Applicable Standard for Galvanization |  | EN ISO 1461 or IS:4736 or an equivalent international standard
| Overall Length | m
| Design span or normal ruling span of Towers | m | 350
| Wind span and weight span of Conductor |  | 1.5 times of Span
| Design Working Load | kg
| Factor of Safety |  | 2
| Minimum Breaking Load | kg
| Overall Height | m
| Center to center between 2 tower legs | m
| Tower width at Ground Level | m
| Maximum width of tower(Foundation width per leg) | m
| Wind zone | 4 | 4, 5; As per IS 802
| Circuit on Towers |  | Single or double
| Angle of Deviation |  | As per site condition
| Phase to Phase Clearance - Horizontal | m | 2.75 and as per Altitude
| Phase to Phase Clearance - Vertical | m | 1.75 and as per Altitude
| Insulator Types |  | Disc
| Conductor |  | ACSR DOG/ ACSR WOLF
| Complete Earthing set as per specification provided | yes/no | yes
3 | Steel Tubular Pole
Manufacturer
Country of Origin
Years of Manufacturing Experience
| Reference Standard |  | IS 2713
| Pole Designation (as per IS 2713) |  | 410 SP-57, 410 SP-72 and heaviest pole in each other length
| Length of Poles | m | 9, 10, 11, 12, 13, 14.5
| Are the poles fully Galvanized? | yes/no | Yes
| Applicable Standard for Galvanization |  | ISO 1461 or IS:4736 or an equivalent international standard
| Approximate Weight (excluding the weight of galvanization, base plate and pole cap) | kg | As per IS 2713
| Planting Depth | m | As per Drawings
4 | Steel Cross Arm Channel and Angle Braces |  | To be completed for all types of components
Manufacturer
Country of Origin
| Reference Standard |  | IS: 2062-2011 and IS 808 -1989
| Dimensions |  | Adhering to Drawings and Detail Design by Contractor
| Is the cross arm and angles fabricated from hot-rolled steel sections? | yes/no | Yes
5 | Pole Clamps, Steel Bolts and Nuts
Manufacturer
Country of Origin
| Reference Standard |  | IS: 2062-2011 and IS 808 -1989
| Dimensions |  | Adhering to Drawings and Detail Design by Contractor and as required on the location of the Poles
| Is the cross arm and angles fabricated from hot-rolled steel sections? | yes/no | Yes
6 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
7 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## A2. ACSR Conductor and Hardware
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A2 | ACSR Conductor and Hardware
1 | ACSR Conductor |  | To be filled Separately for all types used
Manufacturer
Country of Origin
Years of Manufacturing Experience
| Applicable standard |  | IS 398
| Type |  | ACSR DOG/ ACSR WOLF
| Nominal Aluminum Area | sq mm | 100/150
2 | Mid Span Compression Connectors |  | To be filled Separately for all types used
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable Standard
Model No.
| Type |  | Compression
| Current Rating | A | 500
Material
Outer Sleeve
Inner Sleeve
Dimension of Compression Joint for Aluminum part
| Outer | mm
| Inner | mm
Dimension of Compression Joint for Steel part
| Outer | mm
| Inner | mm
| Minimum Failing Load | kN
Electrical Resistance at 20 deg. C
| Size | mm
| weight | Kg
Markings
3 | Parallel Groove (PG) Clamps
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable Standard
Type/Model No.
| Main Conductor |  | WOLF
| Branch Conductor |  | WOLF
| Current Rating | A | 500
Type of Connection
Construction
Body Material
Screw Material
| Bolts size | mm
| Tightening torque | Nm
| Size | mm
| weight | Kg
Markings
4 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
5 | Informative Data, To be filled separately for each equipment
Manufacturer
Submitted for the required ratings
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## A3. Insulators
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A3 | Insulators
1 | Pin Insulator
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standards |  | IS 731-1971, IS 2486, IEC 60815
| Marking as per specifications | yes/no | Yes
| Highest system voltage | kV | 36
| Rated voltage | kV | 33
| Creepage distance (minimum) | mm | 600
| Wet power frequency withstand voltage | kV | 75
| Impulse withstand voltage | kV | 170
| Puncture power frequency voltage (minimum) | kV | 180
| Visible discharge voltage (Effective) | kV | 27
| Cantilever strength | kN | 10
| GI pin head |  | Large
2 | Disc Insulator
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standards |  | IS 731-1971, IS 2486, IEC 60815
| Marking as per specifications | yes/no | Yes
| Highest system Voltage | kV | 12
| Rated Voltage | kV | 11
| Porcelain Diameter (minimum) | mm | 255
| Spacing | mm | 145
| Creepage Distance (minimum) | mm | 320
| Power Frequency Puncture withstand Voltage |  | 1.3 x Actual dry flashover voltage
| Wet Power Frequency Withstand Voltage | kV | 45
| Impulse Withstand Voltage | kV | 75
| Puncture Power Frequency Voltage (minimum) | kV | 105
| Visible Discharge Voltage | kV | 9
| Mechanical Strength | kN | 70
| Ball and Socket Size |  | 16 mm
| Applicable Standard for Special Characteristics |  | IS: 3188-1980
3 | Disc Insulator Fittings
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standard |  | IS: 2486
| Steel Classification |  | As per specification
| Ferrous parts are galvanized As per IS 2629 – 1985? | yes/no | Yes
| Thickness of Galvanizatiioin | micron
| Cotter Pins are Stainless Steel? | yes/no | Yes
| Ultimate Strength of Fittings | kN
4 | Insulator Pins
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standard |  | IS: 2486
| Type of steel used |  | Hot rolled steel
| Head type |  | Large L300N
| Total length | mm | 450
| Stalk length | mm | 300
| Shank length | mm | 150
| Minimum failing load | kN | 10
5 | Pin Insulator Tie
Submitted for the required ratings
Country of Origin
Years of Manufacturing Experience
Model No.
| Material Description furnished? | yes/no | yes
Aluminum clad steel wire
| Bidder Certitifies that all items offered are suitable for use with ACSR "DOG" and "WOLF" conductors? | yes/no | yes
| Bidder Certitifies that all items offered are suitable for use with insulators specified in specifications? | yes/no | yes
| Holding Rating of Top tie for "DOG" | kg
| Holding Rating of Double support Top tie for "DOG" | kg
| Holding Rating of Side tie for "DOG" | kg
| Holding Rating of Double support Side tie for "DOG" | kg
| Holding Rating of Top tie for "WOLF" | kg
| Holding Rating of Double support Top tie for "WOLF" | kg
| Holding Rating of Side tie for "WOLF" | kg
| Holding Rating of Double support Side tie for "WOLF"" | kg
6 | Steel Wire Strand Grip
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Material Description furnished? | yes/no | yes
| Bidder Certitifies that steel strand grip offered is suitable for use with insulator; stay set and stay wire specified in specifications? | yes/no | yes
| Holding Rating of Grip for 7/8 SWG | kg
| Holding Rating of Grip for 7/8 SWG | kg
7 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
8 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## A4. Stays
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A4 | Stays
1 | Stay
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
Applicable Standards
| Marking as per specifications | yes/no | Yes
| Length of stay rod | m | 2.44
| Diameter of stay rod | mm | 19
| Ultimate tensile strength of stay rod and turn-buckle | kg/ sq cm | 4200
| Minimum breaking load | kg | 10454
| Length of threaded portion | mm | 300
| Thimble shape |  | Suitable for Stay wire of 7/8, 19/8 and as per approved design
| Thimble section |  | 18 SWG min.
| Stay plate section | mm | 600 x 600 x 6
| Eyebolt length | mm | 300
| Eyebolt diameter | mm | 16
2 | Stay Wire
Manufacturer
Country of Origin
Years of Manufacturing Experience
| Applicable Standard |  | IS 2141-2000
| Applicable Standard for galvanization |  | IS 4826-1979, BS 183-1972
| Steel Wire Size | (Nos of wire/SWG) | 7/8, 19/8 or as per approved design
| No. of Wire | Nos | 7
| Diameter of Each wire | mm | 4
| Strand Diameter (Overall) | mm | 12
| Overall Cross Sectional Area | sq mm | 88
| Steel Quality |  | Gr. 700
| Minimum Tensile Strength of Steel | N/sq mm | 700
| Ultimate Tensile Strength | N/sq mm
| Min. Breaking load of single wire | kN | 8.8
| Min. Breaking load of strand | kN | 54.9
| Approximate Weight | kg/km
| Minimum weight of Wire in each reel | kg | 100
| Left hand Lay | yes/no | Yes
| Minimum Weight of Zinc Coating | g/sq mm | As per IS 4826-1979, BS 183-1972
3 | Stay Insulator
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standard |  | IS: 5300-1969
| Marking as per specification? | yes/no | Yes
| IS Designation |  | C
| Length | mm | 140
| Diameter | mm | 85
| Cable Hole Diameter | mm | 25
| Creepage Distance (minimum) | mm | 57
| Minimum failing load | kN | 88
Power Frequency Withstand Voltage
| Dry | kV | 27
| Wet | kV | 13
4 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
5 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## A5. ADSS
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A5 | ADSS Cable
1 | ADSS Cable Properties |  | Fill Separately, if required for Approach Cable
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable Standards |  | IEC 60794
| Marking as per specifications | yes/no | Yes
| Fiber Count | no. | 48
Cable Structure
| Fiber no. per tube | no.
| Loose tube | no.
| Central Strength member | material | FRP
| Inner Sheath | mm | ≥1.0
| Outer Sheath |  | ≥1.5
| Cable diameter | mm
| Cable weight | mm
| Maximum Span | m | 200
Minimum Bending Radius
| Installation |  | 25 x cable diameter
| Operation |  | 12.5 x cable diameter
| Cable weight | mm
| Outer Sheath | % | ≥1.2
2 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
3 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## B1. Power Transformer
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
A | Power Transformer
1 | General
Manufacturer
Place of manufacture/ testing
| Applicable Standards |  | IEC 60076
| Type |  | Three Phase
2 | Ratings
| Rated power of Transformer (ONAN) | mVA | As per Price Schedule
| Rated power of Transformer (ONAF) | mVA | As per Price Schedule
| Rated frequency | Hz | 50
| Ambient temperature | °C | 45 or as per scope of supply
| Maximum service altitude | meter | As per Scope of Supply
Temperature rise limit at all tap-changer settings and 10 % over- or under-excitation
| - oil I top | K | 50
| - windings I average | K | 55
| Manufacturer for winding temperature indicator |  | Messko, Germany or Equivalent
| Manufacturer for oil temperature indicator |  | Messko, Germany or Equivalent
| Hottest Spot Temperature in Winding Limited to | K
Rated voltages (no-load):
| - HV winding | kV | 33
| - LV winding | kV | 11
Maximum Voltage
| - HV winding | kV | 36
| - LV winding | kV | 12
Type of tank
| Tank fully vacuum-proof |  | Yes
| Number of windings |  | 2
| Vector group |  | Dyn11
| Magnetic flux density at core and yoke at nominal voltage and frequency | T | >1.6
| Short Circuit Level |  | 25 kA at 33 kV
| Short circuit capacity |  | (according to IEC 60076-5)
Sound pressure
Transformer and tap changing equipment energized and at noload [G]
Pressure relief device min pressure settings
| No-load current (lo/ln) | % | < 1% of rated current
3 | Core design:
- core form
| - type |  | CRGO
- source
- losses
4 | Tap Changer:
| Type of tap changer (On/Off Load) |  | Off Load (1, 3 MVA); On load (8, 16 MVA)
| Tapping range | % | +10% to -10%
| Number of steps | steps | Off Load 9 and On Load 17
| Principal tapping | kV | 33
| Control Suitable for |  | Remote, Local, Auto, Manual, Parallel and Master Slave Operation
Rated Voltage for Drive Motor
| Manufacturer |  | Maschinenfabrik Reinhausen (MR) Germany or ABB Sweden or equivalent
5 | Insulation oil:
- manufacturer
| - type |  | Mineral Oil
| - specification of oil |  | As per IEC 60296
| Approximate Volume of Oil | liters
| Type of Oil Preservation System |  | Conservator Type with Urethane air cell
Volume of Conservator
Volume of Oil between highest and lowest levels
6 | Windings
| Winding Material |  | Copper
Winding insulation design:
| - HV winding |  | Uniform
| - LV winding |  | Uniform
Insulation Level/ HV winding
| - lightning impulse level | kV | 170
| - power frequency withstand voltage | kV | 70
Insulation Level/ LV winding
| Submitted for the required ratings | kV | 75
| - power frequency withstand voltage | kV | 28
| - insulation levels shall be coordinated with actually transferred over-voltages | yes/no | Yes
Method of transformer neutral earthing:
| Primary (HV) |  | Not Applicable
| Secondary (LV) |  | Solid Grounded
Maximum Current Density at Rated Power
| In HV Windings | A/sq mm | 2.5
| In LV Windings | A/sq mm | 2.5
7 | Clearances
| Minimum Clearance in air HV/LV | mm | As per IEC
| Minimum Clearance between phases | mm | As per IEC
| Minimum Clearance between phaes and ground | mm | As per IEC
8 | Cooling and Operation Details
| Cooling method |  | ONAN/ONAF
| Noise level (LpA) at a measuring distance of 2 m (all forced cooling in operation) | dB (A) | As per NEMA standard
| Full power output at all tap positions under specified conditions | yes/no | Yes
| Continuous operation within specified temperature rise limit at over- and under-excitation | % | As per IEC 60076
| No. of Connected Fans | Nos
| No. of Standby Fans | Nos
| Rated Voltage for Fans | V | 400/230
Adjustable Control Gear
9 | Bushings
HV bushings
- manufacturer
- type
| - rated current | A | As per Price Schedule from values provided in IEC 60137
| - power frequency test voltage | kV | 77
| - lightning impulse level | kV | 170
| - minimum creepage distance | mm | 25 mm/kV
LV bushings (outdoor type)
- manufacturer
| - type |  | Oil to Air
| - rated current | A | As per Price Schedule from values provided in IEC 60137
| - power frequency test voltage | kV | 30
| - lightning impulse level | kV | 75
| - minimum creepage distance | mm | 25 mm/kV
10 | Bushing and Neutral Current Transformers
Type and Voltage Class
Number of Cores
| HV | Nos | 1/phase
| LV | Nos | 1/phase
| NCT | Nos | 2
| Accuracy Class |  | PS
| Burden | VA
| Maximum Resistance of Secondary Winding | Ohm
Knee Point Voltage
Magnetising Current at Knee Point Voltage
11 | Guaranteed Losses
| No-load losses at rated voltage and frequency | kW
Load losses at 75 °C and rated current and at HV principal tapping
i. | for ONAN cooling | kW
ii. | for ONAF cooling | kW
| Power Consumption of Cooling Plant at full load | kW
12 | Impedance at 75 °C and rated current and frequency |  | Min 5% for 1, Min 7% for 3, MVA and min 8% for 6/8 and 16 MVA
| - tap changer in position "1" | %
| - tap changer in position "9" | %
| - tap changer in position "17" | %
Short circuit impedance at 75 °C and 100% of rated power:
13 | Efficiency at 75 °C winding temperature
| - at 100% load | kW
| - at 75% load | kW
| - at 50% load | kW
Load % of full load and power factor at which maximum efficiency occurs
14 | Voltage regulation at 75 °C and rated power
| - at unity power factor | %
| - at 0.85 power factor | %
15 | No load current in percentage of rated current referred to HV and 50 Hz
| - at 100% rated voltage | A
| - at 90% rated voltage | A
| - at 110% rated voltage | A
16 | Tests
| Routine tests according to IEC 60076 and Specifications |  | On each unit
| Lightning impulse test (lines only) |  | On each unit
Full wave
| - HV winding | kV | As per IEC 60076
| - LV winding | kV | As per IEC 60076
Chopped wave
| - HV winding | kV | As per IEC 60076
| -LV winding | kV | As per IEC 60076
| Separate source AC voltage withstand test |  | On each unit
| - HV winding | kV | As per IEC 60076
| - LV winding | kV | As per IEC 60076
| Induced AC withstand voltage tests (ACSD), acc. to IEC 60076-3, sub-clause 12 (phase-to-ground and phase-to-phase) |  | On one unit
| - test voltage / HV winding | kV | As per IEC
| - test voltage / LV winding | kV | As per IEC 60076
| Test temperature rise (at all kinds of cooling and at overloads as below) |  | On one unit
| Test of noise level (special test) |  | On one unit
| All other type tests and special tests according to the Specification |  | On one unit
15 | Masses and Dimensions
Transformer masses:
| - total mass | kg
| - transportation mass | kg
| - untanking mass | kg
| - mass of insulation oil | kg
Overall dimensions including bushings:
| - height | mm
| - depth | mm
| - width | mm
Shipping dimensions:
| - height | mm
| - depth | mm
| - width | mm
| Height of crane hooks | mm
Minimum space requirement for the transformer bays (civil works):
- depth
- width
16 | Information to be Submitted with the Tender
Dimension drawing showing the main dimensions nd physical arrangements of major components
Detailed descriptions or leaflets of:
- Arrangement and insulation of windings
- Core and tank
- Conservator and breather
- Tap changer
- Measuring/ monitoring instruments
- Transformer auxiliaries
- Control and marshalling cubicle
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required rating | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
17 | Informative Data
Transformer
Manufacturer
Place of Manufacturing
| Main Dimensions (W x D x H) | m
| Main Dimensions for transportation (W x D x H) | m
| Weight of the transformer inclusive of oil and accessories | t
| Oil weight | t
| Weight for transportation | t
Maximum permitted acceleration during transport
| Lengthwise (x) | m/s2
| Crosswise (y) | m/s2
| Vertical (z) | m/s2
Manufacturers of Accessories
Conservator for transformer
Current transformer
Temperature sensors Pt 100 for oil and winding
Contact thermometers for oil and winding
Control cubicle
Gas relay
Oil level gauge
Wheels
Pressure relief / Explosion vent

## C1. 33 kV System
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
C | 33 kV System
1 | General
Manufacturer
Place of manufacture
| Standards |  | IEC 62271
Type of switchgear, designation
Type tested:
| -each component |  | Yes
2 | Common Characteristics
| Rated voltage | kV | 36
| Nominal system voltage | kV | 33
| Rated frequency | Hz | 50
| Rated power frequency withstand voltage | kV | 70
| Rated lightining impulse withstand voltage | kV peak | 170
| Rated current of busbar feeder | A | 800
| Rated short time withstand current (1 s) | kA rms | 25
| Rated peak withstand current | kA peak | 62.5
| Maximum permissible ambient temperature | °C | As per IEC
| Remote Operability, Unmanned Substation |  | Yes
3 | Circuit Breaker
Designation
Manufacturer
| Standards |  | IEC 62271
| Type |  | Three Pole, VCB, Outdoor
| Pole Breaking |  | Three, Gang Operated
| Rated voltage | kV | 36
| Nominal system voltage | kV | 33
| Rated Frequency | Hz | 50
Rated withstand voltages phase to earth:
| -lightining impulse | kV | 170
| -power frequency | kV | 70
| Rated current | A | 630/800/1250
| Rated short circuit breaking current | rms KA | 25
| Rated making current | peak kA | 62.5
| First pole to clear factor |  | 1.3
| Breaking time | ms | 60
| Opening time | ms | 40
| Closing time | ms | 100
| Close open time | ms | 120
| Rated cable and line charging breaking current | A
Operating mechanism
| - type |  | Motor-Spring
| - number per three phase circuit breaker | pcs | 1 for each phase
| - rated operating sequence |  | O-0.3s-CO-3min-CO
| - number of closing coils | pcs | 1
| - number of tripping coils | pcs | 2
| - rated control voltage | VDC | 110
| -operating noise level (one CB) at 1m distance | dB ( A ) | As per NEMA
Number of CO operations before overhaul
| - at no load mechanical | CO | 10000
| - at rated current | CO
| - at rated short circuit circuit current | CO
| Operating voltage of closing and tripping coil | VDC | 110
| Operating voltage range of closing coil | % of rated voltage | 85 - 110%
| Operating voltage range of tripping coil | % of rated voltage | 70 - 110%
| Spring charging motor capacity | kW
| Spring charging motor rated voltage | V DC | 110
| Closing and Tripping current | A
| Creepage Distance | mm/kV | 25
| Thickness of sheet steel of cubicle | mm | 2
| Number of auxiliary contacts | No | 6NO, 6NC, 6MBB
Temperature rise above 45 deg C ambient at normal rated current
| Contacts | deg Celsius
| Submitted for the required ratings | deg Celsius
| No. of operation | No | 5000
4 | Load Break Switch
Designation
Manufacturer
| Standards |  | IEC 62271-103
| Type |  | Load Break Switch, Outdoor (IP67)
| Pole Breaking |  | Three, Gang Operated
| Rated voltage | kV | 36
| Nominal system voltage | kV | 33
| Rated Frequency | Hz | 50
Rated withstand voltages phase to earth:
| -lightining impulse | kV | 170
| -power frequency | kV | 70
| Rated current | A | 40/630/800/1250
| Rated short circuit breaking current | rms KA | 25
| Rated making current | peak kA | 62.5
| Mounting |  | Pole/Gantry Mounted
Temperature rise above 45 deg C ambient at normal rated current
| Contacts | deg Celsius
| Terminals | deg Celsius
5 | Disconnecting and Earth Switch
| Type |  | 3 pole, single throw, outdoor, center rotating
Designation
Manufacturer
| Standards |  | IEC 62271-102
| Rated voltage | kV | 36
| Nominal system voltage | kV | 33
| Rated Frequency | Hz | 50
Rated withstand voltages phase to earth:
| -lightining impulse | kV | 170
| -power frequency | kV | 70
| Rated current | A | 630/800/1250
| Rated short circuit breaking current | rms KA | 25
Operating mechanism
| - type |  | Motor+manual
| - number of drives per 3 phase | nos | 1
| - drive gear | yes/no | yes
| - operating time | s
| - closing time | s
| - control voltage | VDC | 220
| Number of CO operations before overhaul | CO | 2000
| Type of Interlock furnished |  | Electrical and Mechanical
Temperature rise above 45 deg C ambient at normal rated current
| Contacts | deg Celsius
| Terminals | deg Celsius
Clearance
| Between live parts and ground | mm
| Between fixed contact and blade in open position | mm
Material
| Materials for main contacts |  | Copper Alloy
Materials for Terminals
| Electrical endurance class of Earth Switch according to IEC |  | E0
6 | 33 kV Power Fuse
Designation
Manufacturer
| Standards |  | IEC 60282-2
| Type |  | Single Pole, Single Throw, Drop Out, Hook Stick Operated, Outdoor Type
| Rated voltage | kV | 36
| Nominal system voltage | kV | 33
| Rated Frequency | Hz | 50
Rated withstand voltages phase to earth:
| -lightining impulse | kV | 170
| -power frequency | kV | 70
| Rated current | A | 4
| Rated short circuit breaking current | rms KA | 25
| Fuse Rating | A
Fuse Type
| Mounting Position |  | Vertical
| Number of Pole |  | Three
Type of Contact
Materials of Contact Service
| Air gap between pole of phase | mm
| Creepage Distance | mm/kV | 25
7 | Current Transformer
| Type |  | Ring Type
Designation
Manufacturer
| Standards |  | IEC 61869
| Number of cores | pcs | As per requirement
| Rated current | A | As per SLD
| Accuracy/Class |  | 0.2,5P20,PS
| Rated burden | VA
| Rated power frequency withstand voltage | kV | 70
| Rated lightining impulse withstand voltage | kV | 170
| Overload Factor | % | 200
| Creepage Distance | mm/kV | 25
| Insulation Class |  | E
8 | Potential Transformer
| Type |  | Inductive type, Outdoor, with Fuse
Designation
Manufacturer
| Standards |  | IEC 61869
| Number of cores | pcs | As per requirement
Rated voltage
| - Primary winding | kV | 33/√3
| - Secondary winding | V | 0.11/√3
| Maximum Primary Voltage | kV | 36/√3
Rated power frequency withstand voltage
| - Primary winding | kVrms | 75
| - Secondary winding | kVrms
| Rated lightining impulse withstand voltage | kV | 170
| Accuracy/Class |  | 0.2, 3P
| Burden | VA
| Total thermal rating | VA
| - rated burden | VA
- rated voltage factor
| Creepage Distance | mm/kV | 25
Over Voltage Factor
| 30 seconds |  | 1.1
| Continuous |  | 1.5
Temperature rise above 45 deg C ambient at normal rated current
| - with 1.1 times rated primary voltage continuously | deg C
| - with 1.5 times rated voltage for 30 seconds | deg C
9 | Lightning Arrester
| Type |  | Outdoor, Gapless, Zinc-oxide, procelian housed, Pedestal Mounted
Designation
Manufacturer
| Standards |  | IEC 60099
| Rated voltage | kV | 30
| Energy Absorption Capacity | kJ/kV | min 6
| Nominal Discharge Current | kA | 10
| Minimum Power frequency spark over voltage | kV
| Maximum 1/50 impulse spark over voltage | kV
| Maximum front wave spark over voltage | kV
| Maximum switch surge spark over voltage | kV
Insulation Level
| Impulse withstand voltage | kV | 170
| Power frequency withstand voltage | kV | 70
| Creepage Distance | mm/kV | 25
| Surge Counter with Insulated Base Furnished | m/s2 | yes
10 | Information to be Submitted with the Tender
Dimension drawing showing the main dimensions nd physical arrangements of major components
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
11 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## C2. 33 kV Indicating Instrument
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
C2 | 33 kV Switchgear - Indicating Instruments
1 | General
Manufacturer
Place of manufacture
Applicable Standards
Type
Model No.
Applicable Standard
2 | Control switches
Manufacturer and Country of origin
| Type | Flush type
| Current Rating | A
| Catalog Furnished | yes/no | yes
| Applicable standard |  | IEC
3 | Push Bottom
Manufacturer and Country of origin
Type
| Contact rating continuous | Amp
| Making current | Amp
| Breaking current | Amp
| Catalog Furnished | yes/no | yes
4 | Indicating Lamps
Manufacturer
| Voltage ratings | V
| Wattage | W | <0.5
5 | Ammeter |  | Required (separate)
Manufacturer and Country of origin
| Type |  | Digital
| Accuracy Class |  | 0.5
| Scale |  | Linear
| Range of indication | A | 0-300
| Overloaded range | % | 1.5
VA burden
| Auxiliary DC supply | V | 110
| Catalog furnished | yes/no | yes
| Transducer operated | yes/no | yes
6 | Voltmeter |  | Required (separate)
Manufacturer and Country of origin
| Type |  | Digital
| Accuracy class |  | 0.5
| Scale |  | Linear
| Range of indication | kV | 0-36
| Over scale range | % | 1.1
VA burden
| Auxiliary DC supply | V | 110
| Catalog furnished | yes/no | yes
| Transducer operated | yes/no | yes
7 | Apparent power meter (kVA) |  | Required (separate)
Manufacturer and Country of origin
| Type |  | digital
| Rated voltage | kV | 33/√3:0.11/√3
| Rated current | A | 300-150-75/1
| Current range (Transducer operated) | mA
| Accuracy class |  | 0.5
Scale
| Type of scale |  | linear
| Range of indication |  | 0-10
| VA burden | VA
Current coil
Submitted for the required ratings
| Auxiliary DC supply | V | 110
| Catalog furnished | yes/no | yes
| Transducer operated | yes/no | yes
8 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
9 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## C3. 33 kV Protection Relay
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
C3 | 33 kV Switchgear - Protective Relays
1 | General
Manufacturer
Place of manufacture
Standards
Type
2 | Construction of Control and Relay Panel
| Type |  | Simplex
Manufacturer's type designation
Applicable Standard
| Location |  | Indoor
| Mounting |  | Floor/Trench mounted
| Lifting hooks | yes/no | yes
| Control panel furnished as per specification | yes/no | yes
| Enclosure protection class | IP | IP54
Type of Sheets used
Thickness of sheet metal used
| Load Bearing parts | mm | >3
| Non-load bearing parts | mm | >2
| Painting |  | Light grey RAL 7032
| All instruments, meters, relays and control switches flush or semi flush type |  | flush
3 | Ground Bus
| Material |  | Copper
| Size | mm x mm
4 | Internal Wiring
Type of Insulation
| Voltage Grade of Wires | V | 600
| Cross Section of Wires | sq.mm | min. 2.5
Current Circuit
Voltage and auxiliary circuit
5 | Phase Over Current Relay (50/51) |  | Required (separate)
Manufacturer and Country of origin
| Type |  | Static, Non directional
Manufacturer's type designation
| Applicable standards |  | IEC
| Triple pole or single pole |  | Single*3
| Current setting range | % of rated current | 5-200%
| Operating time at 10 times current settings | m sec | 3
| Reset time | ms
| Characteristics |  | IDMT (Standard inverse)
| Instantaneous unit provided | yes/no | yes
Operating range
NO Contacts
| Insulation test as per IEC | yes/ no | yes
Indication
| Hand reset flags provided | yes/no | yes
| Light emitting diode provided | yes/no | yes
| Auxiliary DC supply | V | 110
| Technical Literature submitted | yes/no | yes
| Test Certificate submitted | yes/no | yes
6 | Earth fault relay (50/51N) |  | Required (separate)
Manufacturer and Country of origin
| Type |  | Static, Non directional
Manufacturer's type designation
| Applicable standard |  | IEC
| Triple pole or single pole |  | Single*3
| Continuous overload capacity | xIn
| Current setting range | % of rated current | 5-80%
| operating time at 10 times current setting | msec | 3
| Characteristics |  | IDMT (Standard inverse)
| Submitted for the required ratings | yes/no | yes
Operating range
NO Contacts
| Insulation test as per IEC | yes/ no | yes
Indication
| Hand reset flags provided | yes/no | yes
| Light emitting diode provided | yes/no | yes
| Auxiliary DC supply | V | 110
| Technical Literature submitted | yes/no | yes
| Test certificate submitted | yes/no | yes
7 | Neutral Time Overcurrent Relay (51N)
Manufacturer and Country of origin
Type
Manufacturer's type designation
| Applicable standard |  | IEC
| Triple pole or single pole |  | Single*3
| Current setting range | % of rated current
| operating time at 10 times current setting | sec | 3
| Reset time | ms
Characteristics
| Instantaneous unit provided | yes/no
| Current setting range | % of rated current
Operating range
| Insulation test as per IEC | yes/ no | yes
Indication
| Hand reset flags provided | yes/no | yes
| Light emitting diode provided | yes/no | yes
| Auxiliary DC supply | V | 110
| Technical Literature submitted | yes/no | yes
| Test certificate submitted | yes/no | yes
8 | Restricted Ground Earth Fault Relay (64REF)
Manufacturer and Country of origin
Type
Manufacturer's type designation
| Applicable standard |  | IEC
| Triple pole or single pole |  | Single
| Continuous overload capacity | xIn
| Current setting range | % of rated current
| operating time at 10 times current setting | sec
Characteristics
| Instantaneous unit provided | yes/no
| Current setting range | % of rated current
| Voltage Setting Range | % of rated voltage
Operating range
| Insulation test as per IEC | yes/ no | yes
Indication
| Hand reset flags provided | yes/no | yes
| Light emitting diode provided | yes/no | yes
| Auxiliary DC supply | V | 110
| Technical Literature submitted | yes/no | yes
| Test certificate submitted | yes/no | yes
9 | Differential Relay (87) |  | Required (separate)
Manufacturer and Country of origin
Standard reference
Type
| Type of Mounting |  | Flush
| Operating time setting | ms | <30
| Sensitivity setting |  | 10-50%xIn
Bias setting
CT ratio Compensating range
| Burden for Current Circuit | VA
| DC Burden | VA
| Tripping Current | A
| Making Current | A
| Closing load (At 110V DC) | A
| Ambient Temperature Range | Deg C
| Auxiliary DC supply | V | 110
| Technical Literature submitted | yes/no | yes
| Test certificate submitted | yes/no | yes
10 | Auxiliary Tripping and Lockout Relay |  | Required (separate)
Manufacturer and Country of origin
Type
Manufacturer's type designation
| Applicable standard |  | IEC
| Operating Time | ms | <15
Does the lockout relay reset by the manually operated or electrically operated reset device
| Is the cut off contact provided to interrupt the operating coil | yes/no | yes
| Contact rating at 125V DC | A
| Auxiliary DC supply | V | 110
| Technical Literature submitted | yes/no | yes
| Test certificate submitted | yes/no | yes
11 | Break Fail Lockout Relay, 86K |  | Required (separate)
| DC Voltage Rating | V | 110
Nos of electrically separate NO and NC Contacts
12 | Break Failure Lockout Relay BF |  | Required (separate)
| DC Voltage Rating | V | 110
Nos of electrically separate NO and NC Contacts
| Technical Literature submitted | yes/no | yes
| Test certificate submitted | yes/no | yes
13 | Overvoltage Relay(59)
Manufacturer and country of origin
| Type |  | Static, Non-directional
| Applicable standard |  | IEC
| Instantaneous unit provided | yes/no | yes
| Insulation test according to IEC | yes/no | yes
Indication
| Hand reset flags provided | yes/no | yes
| Light emitting diode provided | yes/no | yes
| Auxiliary DC supply | V | 110
14 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
| Is Manufacturer ISO 9001 holder? | yes/no | yes
| Technical literature submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
15 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## D1. 12 kV System
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
D | 12 kV Switchgear
1 | General
Manufacturer
Place of manufacture
| Standards |  | IEC 62271 and relevant IEC Standards
| Type |  | 3 phase, Indoor
| Number of cubicles | Nos.
| Rated voltage | kV | 11
| Maximum operating voltage | kV | 12
| Rated frequency | Hz | 50
| Rated busbar current | A
| Temperature rise at ambient air of +40 oC | K | As per IEC
| Rated short time current (1 s) | kA rms | 25
| Rated peak withstand current | kA peak
| Rated power frequency withstand voltage (1 min) | kV rms
| Rated lightning impulse withstand voltage | kV peak
| Rated supply voltage of auxiliary circuits | V | 110
| Type and material of support insulators |  | Epoxy
| Thickness of sheet steel | mm
Protection class
2 | Busbars
Manufacturer
Place of Manufacturing
Type designation
Type of conductors
| Material |  | Copper
| Cross-section | sq.mm
| Cross-section of branch off | sq. mm
| Clearance between phases | mm
| Phase-earth clearance | mm
| Temperature rise of busbars at rated current | K
| Distance between busbars | mm
| Distance between busbars and ground | mm
Busbar Insulation Type
3 | Cubicles
Manufacturer
Place of Manufacturing
Reference standard
Type designation
4 | Circuit Breaker (CB)
| Type |  | Vacuum, Draw Out Type
| Rated frequency | Hz | 50
| Rated voltage | kV | 11
| Maximum operating voltage | kV | 12
| Rated current at ambient temperature of +50 ac | A | 30
Rated breaking current:
| - symmetrical component | kA | 25
| - asymmetrical component | %
| Rated peak-making current | kA peak
| Rated short time current (1 s) | kA rms | 25
| Rated small inductive breaking current | A | As per IEC
Recovery voltage parameters
| - rate of rise | kV rms | As per IEC
| -peak | kV peak | As per IEC
| Rated power frequency withstand voltage | kV voltage
| Rated lightning impulse withstand voltage | kV
| Rated operating sequence |  | CO-3min-CO
| Opening time at rated breaking current (till eparation of arcing contacts) | ms | As per IEC
| Total breaking time | ms | As per IEC
| Closing time at rated making current | ms | As per IEC
| Dead time | ms | As per IEC
| Phase-ground creepage distance | mm
| Submitted for the required ratings |  | Copper Alloy
| Mass of circuit breaker (for each type and size) | kg
| Number of CO operations before overhaul | Nos
| - at no load mechanical | Nos | 3000
| - at rated current | Nos
| - at rated short circuit current | Nos
Operating Mechanism
| Type |  | Motorized
| - number of drives per 3 phases | Nos | 1
| - control voltage | V | 110 DC
| - motor rating | W
Closing Coil/ Tripping Coil
| Rated voltage and frequency | V/Hz | 110 V DC
| Maximum operating voltage | V
| Minimum operating voltage | V
| Rated power | W
Number of auxiliary contacts
- closing
- opening
5 | Disconnecting and Earthing Switch |  | To be filled for DS/ES and ES Only as well
| Type |  | Motorized
| Rated current | A | 630
| Rated short time withstand current (1 s) | kA rms | 25
| Operating time, closing I opening | s
Operating mechanism:
| - number of drives per 3 phases | Nos. | 1
| - control voltage | V | 110 DC
| - motor rating | W
| Number of CO operations before overhaul | Nos.
6 | Current Transformers
| Type |  | Ring Type
Designation
Manufacturer
| Standards |  | IEC 61869
| Number of cores | pcs | As per requirement
| Rated current | A | As per SLD
| Accuracy/Class |  | 0.2,5P20,PS
| Rated burden | VA
| Rated power frequency withstand voltage | kV | 28
| Rated lightining impulse withstand voltage | kV | 75
| Overload Factor | % | 200
| Creepage Distance | mm/kV | 25
7 | Voltage Transformer
| Type |  | Indoor use, within Cubicle, with Fuse
Designation
Manufacturer
| Standards |  | IEC 61869
| Number of cores | pcs | As per requirement
Rated voltage
| - Primary winding | kV | 11/√3
| - Secondary winding | V | 0.11/√3
| Maximum Primary Voltage | kV | 12/√3
Rated power frequency withstand voltage
| - Primary winding | kVrms | 28
| - Secondary winding | kVrms
| Rated lightining impulse withstand voltage | kV | 75
| Accuracy/Class |  | 0.2, 3P
| Burden | VA
| Total thermal rating | VA
| - rated burden | VA
- rated voltage factor
| Creepage Distance | mm/kV | 25
Over Voltage Factor
| 30 seconds |  | 1.1
| Continuous |  | 1.5
Temperature rise above 45 deg C ambient at normal rated current
| - with 1.1 times rated primary voltage continuously | deg C
| - with 1.5 times rated voltage for 30 seconds | deg C
8 | Surge Arrester
| Type |  | Indoor, within Cubicle
Designation
Manufacturer
| Standards |  | IEC 60099
| Rated voltage | kV | 9
| Nominal Discharge Current | kA | 10
| Minimum Power frequency spark over voltage | kV
| Maximum 1/50 impulse spark over voltage | kV
| Maximum front wave spark over voltage | kV
| Maximum switch surge spark over voltage | kV
Insulation Level
| Impulse withstand voltage | kV | 75
| Power frequency withstand voltage | kV | 28
| Creepage Distance | mm/kV | 25
| Surge Counter with Insulated Base Furnished |  | yes
9 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
- Busbar systems
Cubicle dimensions:
| -width | mm
| -depth | mm
| - height | mm
| Mass of heaviest cubicle | kg
| Mass of switchgear | kg
Overall dimension of the complete cubicle:
| Weight of complete cubicle with circuit breaker, etc. | kg
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
10 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## D2. 12 kV Indicating Instrument
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
D2 | 12 kV Switchgear - Indicating Instruments
1 | General
Manufacturer
Place of manufacture
Standards
Type
2 | Ammeter |  | Required (Separate for each incomer & feeder panel)
Manufacturer and country of origin
| Type |  | digital
| Numbers |  | 1/phase
| Range of indication | A | 0-1200-for incomer 0-600-for outgoing
| Accuracy class |  | 0.5
| Scale |  | Linear
| Overload range | % | 1.5
| Auxiliary DC Supply | V | 110
| VA Burden | VA
| Catalogue furnished | yes/no | yes
3 | Voltmeter |  | Required (Separate)
Manufacturer and country of origin
| Type |  | digital
| Numbers |  | 1/phase
| Range of indication | kV | 0-15
| Accuracy class |  | 0.5
| Scale |  | Linear
| Overload range | % | 1.1
| Auxiliary DC Supply | V | 110
| VA Burden | VA
| Catalogue furnished | yes/no | yes
4 | Apparent Power meter |  | Required (Separate for each incomer & feeder panel)
Manufacturer and country of origin
Type
| Rated voltage | kV | 11√3:0.11√3
| Rated Current | A | 300-200-100/1
| Accuracy class |  | 0.5
| Range of indication | mVA | 0-15 or 10
| Auxiliary DC Supply | V | 110
| VA burden | VA
Current coil
Voltage coil
| Catalogue furnished | yes/no | yes
5 | kWh Meter |  | Required (Separate for each incomer & feeder panel)
Manufacturer and country of origin
| Type |  | static 3-phase, 4 wire
| Accuracy class |  | 0.2/0.5
| Rated voltage | kV | 11√3:0.11√3
| Rated Current | A | 300-200-100/1
| VA burden | VA
Current coil
Voltage coil
| Auxiliary DC Supply | V | 110
| Reverse rotation locking mechanism provided | yes/no | yes
6 | Annunciators
Manufacturer and country of origin
Type
| Number of active points | No | 4
| Type of mounting |  | Flush
| Replacement of individual inscription plates and lamps from front panel possible | yes/no | yes
| Sequence of operation as per specification | yes/no | yes
7 | Information to be Submitted with the Tender
Submitted for the required ratings
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
8 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## D3. 12 kV - Protective Relay
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
D3 | 12 kV Switchgear - Protective Relays
1 | General
Manufacturer
Place of manufacture
Standards
Type
2 | Construction of Control and Relay Panel
Type
Manufacturer's type designation
Applicable Standard
| Location |  | Indoor
| Mounting |  | Floor/Trench mounted
| Lifting hooks | yes/no | yes
| Control panel furnished as per specification | yes/no | yes
| Enclosure protection class | IP | IP54
Type of Sheets used
Thickness of sheet metal used
| Load Bearing parts | mm | >3
| Non-load bearing parts | mm | >2
| Painting |  | Light grey RAL 7032
| All instruments, meters, relays and control switches flush or semi flush type |  | flush
3 | Instantaneous Time Overcurrent relay |  | 50/51 in SLD
Manufacturer and country of origin
| Type |  | static Non-directional
Manufacturer's type designation
Applicable standard
| No of poles |  | Single*3
| Current setting range | % of rated current | 5-200%
Operating range
| Operating time at 10 times current setting | sec | 3
| Reset time | ms
| Characteristics |  | IDMT (standard inverse)
| Instantaneous unit provided | yes/no | yes
Operating range
NO Contacts
| Insulation test according to IEC | yes/no | yes
Indication
| Hand reset flags provided | yes/no | yes
| Light emitting diode provided | yes/no | yes
| Auxiliary DC supply | V | 110
| Technical literature provided | yes/no | yes
4 | Residual Ground Overcurrent Relay |  | 50/51N in SLD
Manufacturer and country of origin
| Type |  | Static, Non-directional
| Applicable standard |  | IEC
| Continuous overload capacity | xIn
| Current setting range | % of In | 5-80%
Operating range
| Operating time at 10 times current setting | sec | 3
| Characteristics |  | IDMT (standard inverse)
| Instantaneous unit provided | yes/no | yes
NO Contacts
| Insulation test according to IEC | yes/no | yes
Indication
| Hand reset flags provided | yes/no | yes
| Light emitting diode provided | yes/no | yes
| Auxiliary DC supply | V | 110
5 | Overvoltage Relay |  | 59 in SLD
Manufacturer and country of origin
| Type |  | Static, Non-directional
| Applicable standard |  | IEC
| Submitted for the required ratings | yes/no | yes
| Insulation test according to IEC | yes/no | yes
Indication
| Hand reset flags provided | yes/no | yes
| Light emitting diode provided | yes/no | yes
| Auxiliary DC supply | V | 110
6 | Information to be Submitted with the Tender
Layout and dimension drawings showing the main dimensions and physical arrangement of major components with detailed descriptions and leaflets shall be submitted for:
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
| Is Manufacturer ISO 9001 holder? | yes/no | yes
| Technical literature submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
7 | Informative Data, To be filled separately for each equipment
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## E1. Station Transformer
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
E | Station Transformer
1 | General
Manufacturer
Place of manufacture/ testing
| Applicable Standards |  | IEC
| Type |  | Three Phase
2 | Ratings
| Rated Power of Transformer (ONAN) | kVA | 100
| Rated frequency | Hz | 50
| Ambient temperature | °C | 45 or as per scope of supply
| Maximum service altitude | meter | As per Scope of Supply
Temperature rise limit at all tap-changer settings and 10 % over- or under-excitation
| - oil I top | K | 50
| - windings I average | K | 55
Rated voltages (no-load):
| - HV winding | kV | 33
| - LV winding | kV | 0.4/0.23
Maximum Voltage
| - HV winding | kV | 36
| - LV winding | kV | 0.44
| Number of windings |  | 2
| Vector group |  | Dyn11
| Magnetic flux density at core and yoke at nominal voltage and frequency | T | 1.6
| Short Circuit Level |  | 25 kA at 33 kV
| Short circuit capacity |  | 1 s (according to IEC 60076-5)
Sound pressure
3 | Core design:
- core form
- type
- source
- losses
4 | Insulation oil:
- manufacturer
| - type |  | Mineral Oil
| - specification of oil |  | As per IEC 60296
| Approximate Volume of Oil | liters
5 | Windings
| Winding Material |  | Copper
Winding insulation design:
| - HV winding |  | Uniform
| - LV winding |  | Uniform
Insulation Level/ HV winding
| - lightning impulse level | kV | 170
| - power frequency withstand voltage | kV | 70
Insulation Level/ LV winding
| - power frequency withstand voltage | kV | 3
Method of transformer neutral earthing:
| Primary (HV) |  | Not Applicable
| Secondary (LV) |  | Directly Grounded
Maximum Current Density at Rated Power
| In HV Windings | A/sq mm | 2.5
| In LV Windings | A/sq mm | 2.5
6 | Clearances
| Minimum Clearance in air HV/LV | mm | As per IEC
| Minimum Clearance between phases | mm | As per IEC
| Minimum Clearance between phaes and ground | mm | As per IEC
7 | Cooling and Operation Details
| Cooling method |  | ONAN
| Noise level (LpA) at a measuring distance of 2 m (all forced cooling in operation) | dB (A) | As per NEMA standard
8 | Bushings
HV bushings
- manufacturer
- type
| - rated current | A | As per Price Schedule from values provided in IEC 60137
| - power frequency test voltage | kV | 77
| Submitted for the required ratings | kV | 170
| - minimum creepage distance | mm | 25 mm/kV
LV bushings (outdoor type)
- manufacturer
- type
| - rated current | A | As per Price Schedule from values provided in IEC 60137
| - lightning impulse level | kV | 20
| - power frequency test voltage | kV | 10
| - minimum creepage distance | mm | 25 mm/kV
9 | Tap Changing System:
| Type of tap changer (On/Off Load) |  | Off load
| Tapping range | % | +5% to -5%
| Number of steps | steps | 5
| Principal tapping | kV | 0.4
10 | Guaranteed Losses
| No-load losses at rated voltage and frequency | kW
| Load losses at 75 °C and rated current and at HV principal tapping | kW
| Power Consumption of Cooling Plant at full load | kW
11 | Impedance at 75 °C and rated current and frequency |  | Min 4%
| - tap changer in principal tapping | %
| - tap changer in -5% tapping | %
| - tap changer in +5% tapping | %
Short circuit impedance at 75 °C and 100% of rated power:
12 | Efficiency at 75 °C winding temperature
| - at unity pf and rated current 125% | %
| - at unity pf and rated current 110% | kW
| - at unity pf and rated current 100% | kW
| - at unity pf and rated current 75% | kW
| - at unity pf and rated current 50% | kW
| - at unity pf and rated current 25% | kW
13 | Voltage regulation at 75 °C and rated power
| - at unity power factor | %
| - at 0.8 power factor | %
14 | Tests
| Routine tests according to IEC 60076 and Specifications |  | On each unit
| Lightning impulse test (lines only) |  | On each unit
Full wave
| - HV winding | kV | As per IEC 60076
| - LV winding | kV | As per IEC 60076
Chopped wave
| - HV winding | kV | As per IEC 60076
| -LV winding | kV | As per IEC 60076
| Separate source AC voltage withstand test |  | On each unit
| - HV winding | kV | As per IEC 60076
| - LV winding | kV | As per IEC 60076
| Induced AC withstand voltage tests (ACSD), acc. to IEC 60076-3, sub-clause 12 (phase-to-ground and phase-to-phase) |  | On one unit
| - test voltage / HV winding | kV | As per IEC
| - test voltage / LV winding | kV | As per IEC 60076
| Test temperature rise (at all kinds of cooling and at overloads as below) |  | On one unit
| Test of noise level (special test) |  | On one unit
| All other type tests and special tests according to the Specification |  | On one unit
15 | Masses and Dimensions
Transformer masses:
| - total mass | kg
| - transportation mass | kg
| - untanking mass | kg
| - mass of insulation oil | kg
Overall dimensions including bushings:
| - height | mm
| - depth | mm
| - width | mm
Shipping dimensions:
| - height | mm
| - depth | mm
| - width | mm
Minimum space requirement for the transformer bays (civil works):
- depth
- width
16 | Information to be Submitted with the Tender
Dimension drawing showing the main dimensions and physical arrangements of major components
Detailed descriptions or leaflets of:
- Arrangement and insulation of windings
- Core and tank
- Conservator and breather
- Tap changer
- Measuring/ monitoring instruments
- Transformer auxiliaries
- Control and marshalling cubicle
| Delivery of equipment following award of contract and approval of drawing | months
| ISO 9001 (including design) holder | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
17 | Informative Data
Transformer
Manufacturer
Place of Manufacturing
| Main Dimensions (W x D x H) | m
| Main Dimensions for transportation (W x D x H) | m
| Weight of the transformer inclusive of oil and accessories | t
| Oil weight | t
| Weight for transportation | t
Maximum permitted acceleration during transport
| Lengthwise (x) | m/s2
| Crosswise (y) | m/s2
| Vertical (z) | m/s2
Manufacturers of Accessories
Temperature sensors Pt 100 for oil and winding
Contact thermometers for oil and winding
Control cubicle
Gas relay
Oil level gauge
Wheels
Pressure relief / Explosion vent
m/s2

## E2. ACDB
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
E2 | LOW VOLTAGE DISTRIBUTION SYSTEM
1 | General
Manufacturer
Place of Manufacturer
Standards
Type
| Type tested | yes/no | Yes
| Rated Voltage | V | 1100
| Maximum operating Voltage | V
| Rated Frequency | Hz | 50
| Bus Bar Material |  | Copper
| Bus Bar Insulation Material |  | Air
| Rated short time withstand Current(1s) | kA rms | 25
| Rated peak withsatnd current | kA peak | 50
| Rated power frequency withstand voltage | kV | 2.5
| Protection Class | IP | 42 or better
| Thickness of sheet steel | mm | 2
Dimensions of standard Cubicle:
| Width | mm
| Depth | mm
| Height | mm
| Mass per cubicle | kg approx
2 | Main Distribution Board
| Number of cubicles | Nos | 2
Designation
Type
Standards
| Rating of main CB | A | 2000
| Busbar rating | A | 2000
| Rated short time withstand Current(1s) | kA rms | 20
| Rated peak withsatnd current | kA peak | 50
Dimensions:
| Length | mm
| Width | mm
| Height | mm
| Total weight | kg
3 | Distribution Boards
| Number of cubicles | Nos
Designation
Type
Standards
| Rating of main CB | A | 1000
| Busbar rating | A | 1000
| Rated short time withstand Current(1s) | kA rms
| Rated peak withsatnd current | kA peak
Dimensions:
| Length | mm
| Width | mm
| Height | mm
| Total weight | kg
4 | Information to be Submitted with the Tender
Layout and dimension drawing for each distribution board
Technical leaflets for:
Switchgear and distribution boards
Circuit Breaker
Contactors
Protection relays and auxiliary devices
Typical single line diagrams
5 | Informative Data
Manufacturer
Place of manufacturing
| Submitted for the required ratings | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## F1. Battery System
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
F | Battery and Battery Charger
1 | Battery
Manufacturer
Designation
| Applicable Standard |  | IEC
| Rated Voltage | V DC | 110
| Rated Capacity | Ah | 250
| Type of battery |  | Maintenance Free, Valve Regulated Lead Acid
| Number of Cells | nos
| Number of Units | nos
| Number of Cells in a Unit | nos
| Nominal Voltage Rateing | nos
| Nominal Capacity at 27 deg C at 10h discharge time to cell end voltage 1.75 | Ah
| Amperre capacity at 27 deg C at 10h discharge time to cell end voltage 1.75 | A
Battery Construction type
Type of plates
- Positive (Flat or Tubular)
- Negative
Type of Rack
Rack Dimension
| Float Charging Voltage | V
| Equalizing Charging Voltage | V
| Internal resistance of one cell | ohm
| Short Circuit Current withstand capacity | A
| Float Charging Current | A
| Charging current of a fully discharged battery at 8 hour charging rate | A
| End Voltage of each cell | V
| Charging efficiency of the battery | %
| Max. duration in month, the battery can be kept without charging | month
| Battery life, guaranteed value, | years
2 | Battery Charger
Manufacturer
Designation
| Type of battery |  | Constant voltage
| Output rating | A | 50
| Range of DC voltage variation | ±V
| Maximum AC input | kVA
| Input Voltage/phase | V | 400 V, 3 phase
| Ripple | % | ˂2%
| Emergency of charger at 100% output | %
Temperature rise above ambient of 45 degree C
| a) Solid state elements | oC
| b) Wound elements | oC
| Voltage regulation | % | ±1
Float voltage adjustment
Equalizing voltage adjustment
| Auto equalizing charge provided ? | yes/no | Yes
| Timer for equalizing charge provided ? | yes/no | Yes
| End switching to limit equipment | type
| Manual over-ride switch for selection of float/equalizing charge provided ? | yes/no | Yes
3 | Information to be submitted along with Tender
| ISO 9001 holder (including design) | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
4 | Informative Data
Manufacturer
Submitted for the required ratings
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## F2. DCDB
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
F2 | DC Distribution Board
1 | General
Manufacturer
Place of Manufacturer
Standards
Type
2 | Switchboard
Manufacturer
Place of manufacture
Standards
| Rated voltage | V | 110
| Maximum permissible voltage | V
| Rated current | A
| Rated short-time withstand current | kA | 25
| Rated power frequncy withstand voltage | kV
| Protection class | IP | IP 42 or better
| Thickness of sheet steel | mm | 2
Dimensions:
| - height | mm
| - width | mm
| - depth | mm
| Mass | kg
4.2 | Incomers Circuit Breakers
Manufacturer
Place of manufacture
Type designation
Operating mechanism
Standards
Number of poles
| Rated current | A
| Rated breaking current | kA | 25
4.3 | Outgoing Feeder Circuit Breakers
Manufacturer
Place of manufacture
Type designation
Operating mechanism
Standards
Number of poles
| Rated current | A
| Rated breaking current | kA
4.4 | Busbars
| Material |  | Copper
| Cross-section | mm²
| Rated current | A
| Rated short-time withstand current | kA | 25
4.5 | Measuring Instruments
Class of accuracy
| Size | mm
4.6 | Battery Protection Boxes and Sub-Distribution Boards
110 V DC circuit breakers (to be filled for each type and size)
Type
Manufacturer
Place of manufacture
Standards
| Rated voltage | V
| Rated current | A
| Rated short-time withstand current | kA
| Rated power frequncy withstand voltage | kV
| Protection class | IP | IP 42 or better
| Submitted for the required ratings | mm | 2
Dimensions:
| - height | mm
| - width | mm
| - depth | mm
| Mass | kg
4.7 | Information to be Submitted with the Tender
Layout and Dimension Drawings for Equipment Rooms and Components
Detailed Description and ¦Leaflets of the Proposed Equipments
4.8 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## G1. Cables
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
G1 | CABLES
1 | 11 kV XLPE Cables
Manufacturer
Country of Origin
Years of Manufacturing Experience
Model No.
| Applicable standard |  | IEC 60502, IEC 60228
Cable Type Designation
| Rated Voltage | kV
| Maximum System Voltage | kV | 12
| Rated Voltage between conductor and screen | kV | 6
| Rated Voltage between two conductors | kV | 10
| Power Frequency Withstand Voltage | kV | 28
| Impulse Withstand Voltage (BIL) | kV | 75
Conductor
| Conductor Material |  | EC Grade Aluminum or EC Grade Annealed Copper
| Cross section of the Conductor | sq. mm.
| Is Conductor Stranded? | (yes/no) | yes
Stranded Conductor
i) Number of strands in each core
| ii) Size of strand | Sq. mm.
| iii) Maximum DC Resistance at 20 deg. C | Ohm/km
iv) Class of Stranding
| Number of Cores |  | One/Three/As per SLD
Insulation
| Insulation material and Type Designation |  | XLPE
XLPE Compound manufacturer
| Minimum thickness of insulation | mm | 3.4
| Minimum volume resistivity at 27 deg. C, 70 deg. C and 90 deg. C | Ohm-cm
Sheath
Material for inner sheath, type of sheathing and Type Designation
| Minimum thickness of inner sheath | mm
Material for outer sheath, type of sheathing and Type Designation
| Minimum thickness of outer sheath | mm
Armor
Material
Shape
| Dimension | mm
Conductor Screen
Material
| Thickness | mm
Insulation Screen
Material
| Thickness | mm
Metallic Layer/Screen
Type
Material
| Thickness | mm
| Overall Diameter of the Cable | mm
| Geometric Mean Radius (GMR) of the Cable/Conductor | mm
| Minimum Bending Radius | mm
| Insulation Resistance at 27 deg. C | Ohm/km
| Capacitive Reactance | Ohm/km
| Inductive Reactance | Ohm/km
Conductor Temperature rise during
| Normal Operation | deg. C | 90
| Short Circuit | deg. C | 250
Continuous Current Carrying Capacity
| Continuous Current Carrying Capacity in air and Corresponding assumptions/Conditions of installation | A
| Continuous Current Carrying Capacity under ambient temperature | A
| Continuous Current Carrying Capacity under Cable laid in Covered cable trenches | A
| Continuous Current Carrying Capacity under 3-6 Cables per tray touching each other in Covered cable trenches | A
| Continuous Current Carrying Capacity under ambient temperature for Cable laid in ground | A
Short circuit current
| Short circuit current for 0.1 sec | kA
| Submitted for the required ratings | kA | 25
| Short circuit current for armor 1.0 sec (minimum kA) | kA
| Minimum tensile strength of insulation | kg/sq. cm
| Minimum elongation at break | %
| Minimum tensile strength of sheath | kg/sq. cm
| Minimum elongation at break | %
| Minimum tensile strength of armor | kg/sq. cm
| Minimum elongation at break | %
| Weight of Cable per km | kg/km
| Standard length of Cable per drum | m | min. 500m
| Net weight of cable in drum | kg
Method of Core identification
For Cables up to Five Cores
For Cable with more than Five Cores
Details of Anti Termite Covering
| Longitudinal water tight | yes/no | yes
| Fire Retardant | yes/no | yes
| Moisture Resistant | yes/no | yes
Please indicate in YES or NO whether the following tests have been carried out
| Ageing Test | yes/no | yes
| Loss of Mass Test | yes/no | yes
| Cold Impact Test | yes/no | yes
| Heat Shock Test | yes/no | yes
| Fire Retardant Test | yes/no | yes
Delivery of equipment following award of contract and approval of drawing
| ISO 9001 holder (including design) | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
Details of Marking on Outer Sheath
2 | 1100 V LV Power Cables
Manufacturer
Type of designation
| Standards |  | IEC
| Rated voltage | V | 1100
| Continuous permissible current (in air) | A
Maximum temperature of conductor during
| - continuous operation | °C | 90
| - short circuit duty for 1 s | °C | 250
| Conductor material |  | EC Grade Annealed Copper
| Insulation material |  | Polyethylene
Sheath material
Shield material
Armour material
| Number of cores | pcs
| Conductor cross section | sq mm
Test voltages
| - power frequency withstand | kV
| - direct current | kV
| Nominal bending radius | mm
| Outer cable diameter | mm
| Standard Length of Cable Drum | m | min. 500
| Resistance of 1 m | ohm/m
| Reactance of 1 m | ohm/m
| Insulation Resistance at 27 deg. C | ohm
3 | Control Cables
Manufacturer
Type of designation
| Standards |  | IEC
| Rated voltage | V | 1100
| Test voltage | kV
| Conductor material |  | EC grade annealed Copper
Conductor insulation material
Shield material
Shield Insulation material
Cable sheath material
| Number of cores | pcs
| Conductor cross section | sq. mm
| Minimum bending radius | mm
| Outer cable diameter | mm
| Resistance of 1 m | ohm/m
| Reactance of 1 m | ohm/m
4 | Communication Cables
Manufacturer
Type of designation
| Standard |  | IEC
| Conductor material |  | EC grade annealed Copper
| Conductor diameter | mm
5 | Cable Trays an Accessories
Manufacturer
Type of designation
Material
Type of corrosion protection
6 | Cable Termination Kit |  | To be submitted separately for all kits
Manufacturer
Applicable standard
Type
Insulation level
Maximum design voltage
Impulse withstand voltage(BIL)
| Fire resistance treated | yes/no | yes
| Smoke resistance treated | yes/no | yes
| Stress relief performed | yes/no | yes
| Installation Instruction attached | yes/no | yes
List of Installation Accessories Supplied
7 | Information to be submitted along with bid
| ISO 9001 holder (including design) | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
8 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## G2. Under Ground Cable
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
G2 | Underground Power Cable
1 | Underground Power Cable
Manufacturer
Country of Origin
Year of manufacturing experience
Model No.
| Applicable Standard |  | IEC 60502, IEC 60228
Cable Type Designation
| Rated Voltage | kV | 33
| Maximum System Voltage | kV | 36
| Rated Voltage between conductor and screen | kV
| Rated Voltage between two conductors | kV
| Power Frequency Withstand Voltage | kV | 70
| Impulse Withstand Voltage (BIL) | kV | 170
Conductor
| Conductor Material |  | EC Grade Aluminum
| Cross section of the Conductor | sq. mm.
| Is Conductor Stranded? | yes/no | yes
Stranded Conductor
Number of strands in each core
| Size of strand | Sq. mm.
| vii) Maximum DC Resistance at 20 deg. C | Ohm/km
viii) Class of Stranding
| Number of Cores |  | One Core
Insulation
| Insulation material and Type Designation |  | XLPE
XLPE Compound manufacturer
| Minimum thickness of insulation | mm
| Minimum volume resistivity at 27 deg. C, 70 deg. C and 90 deg. C | Ohm-cm
Sheath
Material for inner sheath, type of sheathing and Type Designation
| Minimum thickness of inner sheath | mm
Material for outer sheath, type of sheathing and Type Designation
| Minimum thickness of outer sheath | mm
Armor
Material
Shape
| Dimension | mm
Conductor Screen
Material
| Thickness | mm
Insulation Screen
Material
| Thickness | mm
Metallic Layer/Screen
Type
Material
| Thickness | mm
| Overall Diameter of the Cable | mm
| Geometric Mean Radius (GMR) of the Cable/Conductor | mm
| Minimum Bending Radius | mm
| Insulation Resistance at 27 deg. C | Ohm/km
| Capacitive Reactance | Ohm/km
| Inductive Reactance | Ohm/km
Conductor Temperature rise during
| Normal Operation | deg. C | 90
| Short Circuit | deg. C | 250
Continuous Current Carrying Capacity
| Continuous Current Carrying Capacity in air and Corresponding assumptions/Conditions of installation | A
| Continuous Current Carrying Capacity under ambient temperature | A
| Continuous Current Carrying Capacity under Cable laid in Covered cable trenches | A
| Continuous Current Carrying Capacity under 3-6 Cables per tray touching each other in Covered cable trenches | A
| Continuous Current Carrying Capacity under ambient temperature for Cable laid in ground | A
Short circuit current
| Short circuit current for 0.1 sec | kA
| Submitted for the required ratings | kA
| Short circuit current for armor 1.0 sec (minimum kA) | kA
| Minimum tensile strength of insulation | kg/sq. cm
| Minimum elongation at break | %
| Minimum tensile strength of sheath | kg/sq. cm
| Minimum elongation at break | %
| Minimum tensile strength of armor | kg/sq. cm
| Minimum elongation at break | %
| Weight of Cable per km | kg/km
| Standard length of Cable per drum | m | min. 500m
| Net weight of cable in drum | kg
Method of Core identification
For Cables up to Five Cores
For Cable with more than Five Cores
Details of Anti Termite Covering
| Longitudinal water tight | yes/no | yes
| Fire Retardant | Yes | Yes
| Moisture Resistant | Yes | Yes
Please indicate in YES or NO whether the following tests have been carried out
| Ageing Test | yes/no | Yes
| Loss of Mass Test | yes/no | Yes
| Cold Impact Test | yes/no | Yes
| Heat Shock Test | yes/no | Yes
| Fire Retardant Test | yes/no | Yes
2 | Information to be submitted along with bid
| ISO 9001 holder (including design) | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
3 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## H1. Substation Auxiliaries
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
H1 | Substation Auxiliaries
H1.1 | Security System
1 | Closed Circuit Television System (CCTV)
1.1 | Matrix Control System
Manufacturer
Type
Description
Technical data
- CPU type
- Type of keyboard
| - Number of videos I/O | pcs
| - Auto/manual camera selection | yes/no
| - Type of interface to ACS |  | LAN
| - Supply voltage | V | 230AC
| - Power demand | W
Dimensions
| - height | mm
| - width | mm
| - depth | mm
| Mass | kg
1.2 | Digital Video Recorder
Manufacturer
Type
Description
Technical data
| - Record rate | ips
- Recording resolution
| - Storage capacity | GB
| - Supply voltage | V
| - Power demand | W
1.3 | Monitors
Manufacturer
Type
Description
Technical data
| - Size | inch
- Sync format
| - Resolution | pixel
| - Supply voltage | V | 230 AC
| - power demand | W
1.4 | Cameras
Manufacturer
Type
Description
Installation
- wall mounted
- pole mounted
- indoor
- outdoor
Lens
| - digital zoom | yes/no
| - auto-focus with manual override | yes/no
| Day/night mode | lux
Protection class
| Temperature range | °C
| Relative humidity | %
2 | Information to be submitted along with bid
Layout and Dimension Drawings for Equipment Rooms and Components
Detailed Description and ¦Leaflets of the Proposed Equipments
3 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## H2. SAS System
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
H2 | Substation Automation System
1 | Server
Manufacturer/Country
Type/Model
Processor
Processor Speed
HDD and RAM
Operating System
2 | Gateway
Manufacturer/Country
Type/Model
Processor
Processor Speed
HDD and RAM
Operating System
3 | Operator Workstation
Manufacturer/Country
Type/Model
Processor
Processor Speed
HDD and RAM
Operating System
4 | Eternet Switch
Manufacturer/Country
Type/Model
Mounting Arrangement
5 | Time Synchronizing Equipment
Manufacturer/Country
Type/Model
Mounting Arrangement
6 | Printer
Manufacturer/Country
Type/Model
Mounting Arrangement
7 | Monitor
Manufacturer/Country
Type/Model
Mounting Arrangement
Include other miscellaneous items if required
8 | Information to be submitted along with bid
| ISO 9001 holder (including design) | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
9 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## H3. Protection System
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
E | Protection System |  | Fill for all relays and accessories, even if not mentioned
1 | General Information
1.1 | General
Manufacturer
Place of manufacturer
| Standards |  | IEC
| Protection- type, designation |  | Numerical
| Years in service | years
Protection Devices
| Type tested acc. To relevant IEC Standards | yes/no
| Module, 19 ' plug-in design | yes/no
| Fully degital processing | yes/no
| Internal/ external bus communication | yes/no
| Protection class | IP
1.2 | Interfaces
| Type of communication protocol/ standards |  | IEC-60870-5-104
| Bus interface for data transfer to CCS | yes/no
| Serial interface for connection of laptop | yes/no
Serial interface for connection of portable protocol printer
1.3 | Tripping/ Signalling Contacts
| Switching voltage | V DC
| permissibel continuous current | A
| Number of auxiliary contacts NO/NC | pcs
1.4 | Digital Tripping Matrix
Software Matrix
1.5 | Special Protection Features
| Trip-cicuits supervision | yes/no
| Local/ remote reset | yes/no
1.6 | Test Equipment
| Manual test set | yes/no
| Automatic test set | yes/no
| Built-in test features | yes/no
1.7 | Rated Input Data
Measuring Circuits:
| - Rated current IN | A | 0.2
| - Rated voltage UN | V | 230
| - Rated frequency fN | Hz
1.8 | Auxiliary Power Supply
| Redundant auxiliary DC-supply for each system | yes/no | yes
| - Supply voltage | V DC | 110
| - DC/DC converter | V/V
1.9 | Cubicle Data
| Thickness of sheet steel | mm
Dimensions:
| - height | mm
| - depth | mm
| - width | mm
| Front glass door | yes/no
| Rear door | yes/no
| Hinged swing frame for relay installation | yes/no
| Protection class | IP | 55
| Mass | kg
1.10 | Climatic Conditions
| Ambient temperature | °C
| Operation temperature range | °C
| Relative humidity range | %
2 | Power Transformer
2.1 | (27) Under Voltage Protection
| Type designation |  | Numerical
Measurement principle
Setting:
| - under voltage U< at fN | X UN
| - delay time | s
| - min response time | ms
| - frequency independent | Hz
2.2 | Submitted for the required ratings
| Type designation |  | Numerical
Measurement principle
Setting·
| - current (in steps 0 1 IN) | X IN
| - delay time | s
| - reset ratio (for max. function) | %
| (for min function) | %
| - trip-time (with no delay) | ms
| - wide frequency range | xfN
2.3 | (51/51 N) Time-delayed Overcurrent Protection
| Type designation |  | Numerical
Measurement principle
Setting:
| - current | xIN
| - delay time | s
| - reset ratio for I>> | %
| - trip time (with no delay) | ms
2.4 | (59/59N) Overvoltage Protection
| Type designation |  | Numerical
Measurement principle
Setting
- inclination characteristic
| - range of voltage setting | % VN
| - time delay | s
| - reset ratio | %
| - pick-up - Alarm stage | %
| - Tripping stage | %
| - drop-out to pick-up ratio | %
| - min. response time | ms
2.5 | (81) Under-Over frequency Protection
| Type designation |  | Numerical
Measurement principle
Setting:
| frequency range | Hz
| time | s
| min. voltage | V
| accuracy of pick-up value reset ratio | %
| Measurement principle | %
Setting:
2.6 | (87T) Transformer Differential Protection
| Type designation |  | Numerical
Measurement principle
Setting
| g, basic setting | X IN
| - v, pick-up ratio | V
Trip-time (max )
| - for ldiff>21N | ms
| - for ldiff <21N | ms
| Accuracy of pick-up of g | %
| Frequency range | Hz
2.7 | Dimensions and Masses
| Number of cubicles per unit | pcs
Dimensions of cubicle assembly:
| - height | mm
| - depth | mm
| - width | mm
| Total mass | Kg
3 | 33 kV AIS
3.1 | (21) Line Distance Protection
| Type designation |  | Numerical
Measurement principle
Setting circular characteristic, R-X diagram
| - impedance | X UN/IN
| - time delay range stage 1 (t1) | s
| range stage 2 ( t1, t2, t3) | s
3.2 | (50/50N) Instantaneous Overcurrent Protection
| Type designation |  | Numerical
Measurement principle
Setting
| - current (in steps 0.1 IN) | X IN
- delay time
| - reset ratio (for max. function) | %
| (for min. function) | %
| trip-time (with no delay) | ms
| wide frequency range | X fN
3.3 | (51/51 N) Time-delayed Overcurrent Protection
| Type designation |  | Numerical
Measurement principle
Setting:
| - current | X IN
| - delay time | s
| - reset ratio for I>> | %
| - trip time ( with no delay) | ms
3.4 | 87BB Busbar Differential Protection
| Type designation |  | Numerical
Measurement principle
Protection settings, setting ranges
- Differential current
- in steps of
- accuracy
- Stabilizing factor k
- in steps of
- special applica tions
- Accuracy
| - Differential current | X IN
- alarm
| - Integration time 50 Hz | ms
| - Operation times | ms
| - tripping time (incl. aux. output voltage) | ms
- they are valid for fault currents ≥
4 | Station Auxilliary System
4.1 | (50/SON) Instantaneous Overcurrent Protection
| Type designation |  | Numerical
Measurement principle
Setting:
| - current (in steps 0.1 IN) | X IN
| - delay time | s
| - reset ratio (for max. function) | %
| (for min. function) | %
| - trip-time (with no delay) | ms
| - wide frequency range | X fN
4.2 | (51/51 N) Time-delayed Overcurrent Protection
| Type designation |  | Numerical
Measurement principle
Setting:
| - current | X IN
| - delay time s | s
| - reset ratio for I>> | %
| - trip time (with no delay) | ms
5 | Dimensions and Masses
| Number of cubicles | pcs
Dimensions of cubicle assembly:
| - height | mm
| - depth | mm
| - width | mm
| Total mass | Kg
6 | Information to be Submitted with the Tender
1) Detailed description and leaflets for each proposed protection device and ancillary equipment
2) Layout and dimension drawings of cubicles/cubicle assemblies
3) Typical diagrams for:
- power supply
- trip circuit with supervision
- trip circuit with supervision
7 | Information to be submitted along with bid
| ISO 9001 holder (including design) | m/s2 | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
8 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## H4. Communication System
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
H4 | Communication System
1 | SDH Equipment |  | STM-4 MADM upto 3 MSP protected directions
| Base Equipment |  | Common cards, Cross Connect/control cards, optical base cards, power supply cards, power cabling, other hardware and accessories including sub racks, patch cord, DDF etc fully equiped
Optical Interface Cards/SFP#
Tributary Cards
2 | Termination Equipment
Include other miscellaneous items if required
3 | Information to be submitted along with bid
| ISO 9001 holder (including design) | yes/no | yes
| ISO 9001 certificate submitted | yes/no | yes
| Type test certificate submitted | yes/no | yes
| Submitted for the required ratings | yes/no
Type test certified by
| User's certificate submitted | yes/no | yes
| Has exported to third country | yes/no | yes
| Copies of relevant standards attached | yes/no | yes
| Outline Drawings and associated GA attached | yes/no | yes
4 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## I1. Earthing System
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
H | Earthing and Lightning System
1 | Above Ground Earthing System
Manufacturer
| Type of conductors |  | Copper
Materials
| Dimensions | mm
| Cross sections | sq. mm
2 | Potential Gradient Control System
Manufacturer
| Conductor Material |  | Copper
| Cross section | sq. mm
3 | Lightning Protection System
3.1 | General
Manufacturer
Type of lightning protection system
Standards
3.2 | Air Terminals
Manufacturer
Materials
| Dimensions Diameter/Length | sq. mm
3.3 | Roof Conductors
Manufacturer
Conductor Material
| Cross section | sq. mm
3.4 | Down Conductors
Manufacturer
Conductor Material
| Cross section | sq. mm
3.5 | Termination and Jointing Materials
Manufacturer
Types
Designations
4 | Ground Conductor
Main ground grid conductor material
| Main ground grid conductor size | sq.mm
Depth of buried main ground conductor
Material of riser
| Cross-section of riser conductor | sq.mm
Type of joint above and below ground level
Ground electrode
Material
| Diameter | mm
| Length | m | as per IEEE80
Fence grounding included
| Cross section of conductor rise for fence ground | sq.mm
| Fence separately grounded by electrode | yes/no | yes
| Calculation for grounding grid length and conductor size furnished | yes/no | yes
| Earthing system designed for | ohm | <1
5 | Information to be submitted along with bid
Layout and Dimension Drawings for Equipment Rooms and Components
Detailed Description and ¦Leaflets of the Proposed Equipments
6 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2

## J1. Illumination System
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
I | Lighting System
1 | Lighting Fixtures
1.1 | LED Lighting Fixture Type 1
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.2 | LED Lighting Fixture Type 2
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.3 | LED Lighting Fixture Type 3
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.4 | Mercury Vapour Lamp Type 4
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.5 | Recessed LED Lamp Type 5
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.6 | Street Lighting Fixture Type 6
Manufacturer
| Type |  | LED
Designation
Submitted for the required ratings
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.7 | Low Energy Lamp Type 7
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.8 | High Capacity Floodlight Fixture Type 8
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.9 | Compact LED Lamp Type 9
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.1 | Security Lighting Fixture ''EXIT'' and ''ESCAPE DIRECTION'' Type 10
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.11 | Portable Floodlight Type 11
Manufacturer
| Type |  | LED
Designation
Battery rating
| Rated voltage | V
| Rated power | W
| Service time until recharging | %
Type of chanrging station
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
1.12 | Portable LED Lamp Type 12
Manufacturer
| Type |  | LED
Designation
Class of light distribution
| Rated voltage | V
| Rated power | W
| Efficiency | %
Installation method
| Protection class | IP
| Overall dimensions | mm
| Mass | kg
2 | LAMPS
2.1 | Low Energy/Compact LED Lamp
Manufacturer
Type
Rated voltage
Rated power
Luminous flux
2.2 | High Pressure Mercury Vapour Lamp
Manufacturer
Type
| Rated voltage | V
| Rated power | W
| Luminous flux | lm
2.3 | LED Tube
Halogen Lamp
Manufacturer
Type
| Rated voltage | V
| Rated power | W
| Luminous flux | lm
3 | 400/230 V Lighting Distribution Boards
Manufacturer
Type
Standards
| Rated Voltage | V
| Rated frequency | Hz
3.1 | Busbars
Type
Material
| Rated current | A
| Rated short -time withstand current (1 s) | kA
| Rated peak current | kA
3.2 | Circuit Breakers
Manufacturer
Type
| Rated Voltage | V
| Rated current | A
| Rated short circuit breaking current | kA
| Rated short circuit making capacity | kA
| Rated short -time withstand current (1 s) | kA
3.3 | Cubicles
| Sheet steel thickness | mm
| Protection class | IP
Dimensions
| - height | mm
| - width | mm
| - depth | mm
| Mass | kg
4 | Socket Outlets 400 V and 230 V
Manufacturer
Type
| Protection Class | IP
m/s2
5 | Switches
Manufacturer
Type
| Protection Class | IP
6 | Information to be submitted along with bid
Layout and Dimension Drawings for Equipment Rooms and Components
Detailed Description and ¦Leaflets of the Proposed Equipments
7 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm

## K1. Miscellaneous
Nepal Electricity Authority
Distribution and Consumer Services Directorate
Distribution System Upgrade and Expansion Project
Technical Data Sheet
To be filled separately for each equipment and manufacturers; Employer's Requirement are subjected to variation as per altitude of installation and climatic condition. The site specific requirement shall be understood after incorporating Altitude Correction Factor as per IEC Standard.
S.N. | Description | Unit | Employer's Requirement | Bid Offer
K | Miscellaneous
1 | Air Conditioner
1.1 | General
Manufacturer
Type
Designation
Place of Origin
1.2 | Capacity
| Cooling | BTU/hr | 1800
| Heating | BTU/hr | 19500
| Compressor |  | Rotary
1.3 | Power Supply
| Power Supply | V/Ph/Hz | 230/Single/50
Power Input (Cooling/heating)
Current
1.4 | Energy Star Rating
| Energy Star Rating |  | > 5
1.5 | Performance
| EER | BTU/hr./W | 10/10
| Air Circulation (Indoor/outdoor) | CFm | > 460/1485
| Moisture Removal | l/hr | > 2.5
| Noise Level (indoor/outdoor) | dB | < 46
1.6 | Operation
| Panel Display |  | LCD
| Remote Controller |  | LCD
1.7 | Features
| Auto Air Swing |  | √
| Speed Setting | Cooling/Fan | 3/3
| Operation Control |  | Microprocessor controlled codeless remote
| Auto Restart |  | √
| Sleep Mode |  | √
| On Timer |  | √
| OFF Timer |  | √
| Dehumidification |  | √
| Chaos Logic |  | √
| Fuzzy Logic |  | √
| Jet Cool |  | √
| Evaporator Type |  | 2 Row
| Evaporator Fin Type |  | Blue fin/Gold fin
| Condenser Fin Type |  | Blue fin/Gold fin
| Refrigerant |  | Eco-friendly (non-CFC)
| Anti-bacteria Filter |  | √
1.8 | Dimensions and Net Weight
| Indoor (LxWxH) | mm
| Outdoor (LxWxH) | mm
| Indoor | kg
| Outdoor | kg
| Warranty |  | Minimum two years (min. five years on compressor)
1.9 | Additional Requirement
| copper pipe with superlon insulation for suction line | m | 4
| copper pipe with superlon insulation for discharge line | m | 4
| PVC pipe for drain | m | 1
Base plate for hanging yes
2 | Flexible Pipe
Manufacturer
Country of Origin
Years of Manufacturing Experience
Applicable standard
Manufacturer Type Designation
| Type |  | Corrugated hard polyethylene
| Thickness of pipe | mm
| Outer diameter of the pipe | mm
| Tensile Strength | N/ sq mm
| Compressive Strength | N/ sq mm
| Submitted for the required ratings | N/ sq mm
3 | Information to be submitted along with bid
Layout and Dimension Drawings for Equipment Rooms and Components
Detailed Description and ¦Leaflets of the Proposed Equipments
4 | Informative Data
Manufacturer
Place of manufacturing
| Dimension (W x D x H) | mm
| Standard drum length | m
| Weight | kg
Shipping Data
| Weight of heaviest package | kg
| Dimension of largest package (W x D x H) | mm
m/s2